## Sheet1
Level | Device |  | Trigger |  |  | Identification | [6 empty] | Parameters | [9 empty] | Kommentar
[13 empty] | Condition | [5 empty] | Reaction
| Model / Manufacturer | Type | Source | Register / Module | Bit | Code |  |  |  | Namespace | Enumerator | Text | Scope | Type | Trigger |  | Acknowledge |  | Dera-ting | Auto Ack. / Restart | Level | Target
[6 empty] | Main | M | B | Full | [5 empty] | Level | Delay | Level | Delay
Hardware | Enasys | IPU | MCU | ErrorIRQ | 0 | 0x20 | X | 2 | 0x20X200 | ERROR_CODES::IPU::v3LV1::MCU | TEMP_TRIP_IGBT_3 | Temp Trip IGBT 3 | SHARC | Extern | [5 empty] | RESTART | SHUTDOWN | CFG_REDUNDANT
Hardware | Enasys | IPU | MCU | ErrorIRQ | 1 | 0x20 | X | 2 | 0x20X201 | ERROR_CODES::IPU::v3LV1::MCU | TEMP_TRIP_IGBT_2 | Temp Trip IGBT 2 | SHARC | Extern | [5 empty] | RESTART | SHUTDOWN | CFG_REDUNDANT
Hardware | Enasys | IPU | MCU | ErrorIRQ | 2 | 0x20 | X | 2 | 0x20X202 | ERROR_CODES::IPU::v3LV1::MCU | TEMP_TRIP_IGBT_1 | Temp Trip IGBT 1 | SHARC | Extern | [5 empty] | RESTART | SHUTDOWN | CFG_REDUNDANT
Hardware | Enasys | IPU | MCU | ErrorIRQ | 3 | 0x20 | X | 2 | 0x20X203 | ERROR_CODES::IPU::v3LV1::MCU | TEMP_TRIP_4 | Temp Trip Board | SHARC | Extern | [5 empty] | RESTART | SHUTDOWN | CFG_REDUNDANT
Hardware | Enasys | IPU | MCU | ErrorIRQ | 4 | 0x20 | X | 2 | 0x20X204 | ERROR_CODES::IPU::v3LV1::MCU | TEMP_TRIP_3 | Temp Trip Grid Choke | SHARC | Extern | [5 empty] | RESTART | SHUTDOWN | CFG_REDUNDANT
Hardware | Enasys | IPU | MCU | ErrorIRQ | 5 | 0x20 | X | 2 | 0x20X205 | ERROR_CODES::IPU::v3LV1::MCU | TEMP_TRIP_2 | Temp Trip Heatsink Sensor | SHARC | Extern | [5 empty] | RESTART | SHUTDOWN | CFG_REDUNDANT
Hardware | Enasys | IPU | MCU | ErrorIRQ | 6 | 0x20 | X | 2 | 0x20X206 | ERROR_CODES::IPU::v3LV1::MCU | TEMP_TRIP_1 | Temp Trip Module Choke | SHARC | Extern | [5 empty] | RESTART | SHUTDOWN | CFG_REDUNDANT
Hardware | Enasys | IPU | MCU | ErrorIRQ | 7 | 0x20 | X | 2 | 0x20X207 | ERROR_CODES::IPU::v3LV1::MCU | DESAT_TRIP_1 | IGBT 1 Saturation | SHARC | Extern | [6 empty] | SHUTDOWN | CFG_REDUNDANT
Hardware | Enasys | IPU | MCU | ErrorIRQ | 8 | 0x20 | X | 2 | 0x20X208 | ERROR_CODES::IPU::v3LV1::MCU | DESAT_TRIP_2 | IGBT 2 Saturation | SHARC | Extern | [6 empty] | SHUTDOWN | CFG_REDUNDANT
Hardware | Enasys | IPU | MCU | ErrorIRQ | 9 | 0x20 | X | 2 | 0x20X209 | ERROR_CODES::IPU::v3LV1::MCU | DESAT_TRIP_3 | IGBT 3 Saturation | SHARC | Extern | [6 empty] | SHUTDOWN | CFG_REDUNDANT
Hardware | Enasys | IPU | MCU | ErrorIRQ | 10 | 0x20 | X | 2 | 0x20X20A | ERROR_CODES::IPU::v3LV1::MCU | INTERN_TRIP_1 | Invalid Dutycycles Phase 1 | SHARC | Extern | [5 empty] | RESTART | SHUTDOWN | CFG_REDUNDANT
Hardware | Enasys | IPU | MCU | ErrorIRQ | 11 | 0x20 | X | 2 | 0x20X20B | ERROR_CODES::IPU::v3LV1::MCU | INTERN_TRIP_2 | Invalid Dutycycles Phase 2 | SHARC | Extern | [5 empty] | RESTART | SHUTDOWN | CFG_REDUNDANT
Hardware | Enasys | IPU | MCU | ErrorIRQ | 12 | 0x20 | X | 2 | 0x20X20C | ERROR_CODES::IPU::v3LV1::MCU | INTERN_TRIP_3 | Invalid Dutycycles Phase 3 | SHARC | Extern | [5 empty] | RESTART | SHUTDOWN | CFG_REDUNDANT
Hardware | Enasys | IPU | MCU | ErrorIRQ | 13 | 0x20 | X | 2 | 0x20X20D | ERROR_CODES::IPU::v3LV1::MCU | POWER_TRIP | Power Trip | SHARC | Extern | [6 empty] | SHUTDOWN | CFG_REDUNDANT
Hardware | Enasys | IPU | MCU | ErrorIRQ | 14 | 0x20 | X | 2 | 0x20X20E | ERROR_CODES::IPU::v3LV1::MCU | OC_TRIP_1 | Overcurrent Phase 1 | SHARC | Extern | [5 empty] | RESTART | SHUTDOWN | CFG_REDUNDANT
Hardware | Enasys | IPU | MCU | ErrorIRQ | 15 | 0x20 | X | 2 | 0x20X20F | ERROR_CODES::IPU::v3LV1::MCU | OC_TRIP_2 | Overcurrent Phase 2 | SHARC | Extern | [5 empty] | RESTART | SHUTDOWN | CFG_REDUNDANT
Hardware | Enasys | IPU | MCU | ErrorIRQ | 16 | 0x20 | X | 2 | 0x20X210 | ERROR_CODES::IPU::v3LV1::MCU | OC_TRIP_3 | Overcurrent Phase 3 | SHARC | Extern | [5 empty] | RESTART | SHUTDOWN | CFG_REDUNDANT
Hardware | Enasys | IPU | MCU | ErrorIRQ | 17 | 0x20 | X | 2 | 0x20X211 | ERROR_CODES::IPU::v3LV1::MCU | SWFREQ_TRIP | Switching Frequency Error | SHARC | Extern | [5 empty] | RESTART | SHUTDOWN | CFG_REDUNDANT
Hardware | Enasys | IPU | MCU | ErrorIRQ | 18 | 0x20 | X | 2 | 0x20X212 | ERROR_CODES::IPU::v3LV1::MCU | RMS_TRIP | RMS Current Error | SHARC | Extern | [5 empty] | RESTART | SHUTDOWN | CFG_REDUNDANT
Hardware | Enasys | IPU | MCU | ErrorIRQ | 19 | 0x20 | X | 2 | 0x20X213 | ERROR_CODES::IPU::v3LV1::MCU | SOFTWARE_TRIP | Software Error | SHARC | Extern | [5 empty] | RESTART | SHUTDOWN | CFG_REDUNDANT
Hardware | Enasys | IPU | MCU | ErrorIRQ | 20 | 0x20 | X | 2 | 0x20X214 | ERROR_CODES::IPU::v3LV1::MCU | V1_TRIP | Grid Overcurrent Phase 3 | SHARC | Extern | [5 empty] | RESTART | SHUTDOWN | CFG_REDUNDANT
Hardware | Enasys | IPU | MCU | ErrorIRQ | 21 | 0x20 | X | 2 | 0x20X215 | ERROR_CODES::IPU::v3LV1::MCU | V2_TRIP | Grid Overcurrent Phase 2 | SHARC | Extern | [5 empty] | RESTART | SHUTDOWN | CFG_REDUNDANT
Hardware | Enasys | IPU | MCU | ErrorIRQ | 22 | 0x20 | X | 2 | 0x20X216 | ERROR_CODES::IPU::v3LV1::MCU | V3_TRIP | Grid Overcurrent Phase 1 | SHARC | Extern | [5 empty] | RESTART | SHUTDOWN | CFG_REDUNDANT
Hardware | Enasys | IPU | MCU | ErrorIRQ | 23 | 0x20 | X | 2 | 0x20X217 | ERROR_CODES::IPU::v3LV1::MCU | V4_TRIP | 24 V Fault | SHARC | Extern | [5 empty] | RESTART | SHUTDOWN | CFG_REDUNDANT
Hardware | Enasys | IPU | MCU | ErrorIRQ | 24 | 0x20 | X | 2 | 0x20X218 | ERROR_CODES::IPU::v3LV1::MCU | V5_TRIP | Module Overcurrent Phase A | SHARC | Extern | [5 empty] | RESTART | SHUTDOWN | CFG_REDUNDANT
Hardware | Enasys | IPU | MCU | ErrorIRQ | 25 | 0x20 | X | 2 | 0x20X219 | ERROR_CODES::IPU::v3LV1::MCU | V6_TRIP | Module Overcurrent Phase B | SHARC | Extern | [5 empty] | RESTART | SHUTDOWN | CFG_REDUNDANT
Hardware | Enasys | IPU | MCU | ErrorIRQ | 26 | 0x20 | X | 2 | 0x20X21A | ERROR_CODES::IPU::v3LV1::MCU | V7_TRIP | Module Overcurrent Phase C | SHARC | Extern | [5 empty] | RESTART | SHUTDOWN | CFG_REDUNDANT
Hardware | Enasys | IPU | MCU | ErrorIRQ | 27 | 0x20 | X | 2 | 0x20X21B | ERROR_CODES::IPU::v3LV1::MCU | UDC_P_TRIP | DC-Link Positive Voltage Fault | SHARC | Extern | [5 empty] | RESTART | SHUTDOWN | CFG_REDUNDANT
Hardware | Enasys | IPU | MCU | ErrorIRQ | 28 | 0x20 | X | 2 | 0x20X21C | ERROR_CODES::IPU::v3LV1::MCU | UDC_N_TRIP | DC-Link Negative Voltage Fault | SHARC | Extern | [5 empty] | RESTART | SHUTDOWN | CFG_REDUNDANT
Hardware | Enasys | IPU | MCU | ErrorIRQ | 29 | 0x20 | X | 2 | 0x20X21D | ERROR_CODES::IPU::v3LV1::MCU | UDC_DIFF_TRIP | DC-Link Voltage Imbalance | SHARC | Extern | [5 empty] | RESTART | SHUTDOWN | CFG_REDUNDANT
Hardware | Enasys | IPU | MCU | ErrorIRQ | 30 | 0x20 | X | 2 | 0x20X21E | ERROR_CODES::IPU::v3LV1::MCU | TACHO_TRIP | Fan Error | SHARC | Extern | [5 empty] | RESTART | SHUTDOWN | CFG_REDUNDANT
DSC | Enasys | IPU | FPGA | ErrorIRQ | 0 | 0x20 | X | 1 | 0x20X100 | ERROR_CODES::IPU::v3LV1::COM | CURRENT_LOOP_TRIP | CurrentLoop Open | SHARC | Extern | [5 empty] | RESTART | SHUTDOWN | CFG_REDUNDANT
DSC | Enasys | IPU | FPGA | ErrorIRQ | 1 | 0x20 | X | 1 | 0x20X101 | ERROR_CODES::IPU::v3LV1::COM | WATCHDOG_TRIP | Watchdog Timeout | SHARC | Extern | [6 empty] | SHUTDOWN | CFG_REDUNDANT
DSC | AixControl | CCU Slave | Sharc | COMInspector | 2 | 0x20 | X | 1 | 0x20X102 | ERROR_CODES::IPU::v3LV1::COM | SLAVE_UNREACHABLE | Slave unreachable | SHARC | BOOL |  | 1 |  | 0 |  | AUTOACK | WARNING | SYSTEM
DSC | AixControl | CCU Slave | Sharc | ErrorHandler | 3 | 0x20 | X | 1 | 0x20X103 | ERROR_CODES::IPU::v3LV1::COM | SLAVE_ERROR | Slave error | SHARC | BOOL |  | 0 |  |  |  | RESTART | SHUTDOWN | CFG_REDUNDANT
Hardware | Enasys | IPU | MCU | ErrorIRQ | 0 | 0x40 | X | 2 | 0x40X200 | ERROR_CODES::IPU::vDCDC::MCU | TEMP_TRIP_IGBT_3 | Bit 0 | SHARC | Extern | [5 empty] | RESTART | SHUTDOWN | CFG_REDUNDANT
Hardware | Enasys | IPU | MCU | ErrorIRQ | 1 | 0x40 | X | 2 | 0x40X201 | ERROR_CODES::IPU::vDCDC::MCU | TEMP_TRIP_IGBT_2 | Bit 1 | SHARC | Extern | [5 empty] | RESTART | SHUTDOWN | CFG_REDUNDANT
Hardware | Enasys | IPU | MCU | ErrorIRQ | 2 | 0x40 | X | 2 | 0x40X202 | ERROR_CODES::IPU::vDCDC::MCU | TEMP_TRIP_IGBT | Temp Trip IGBT | SHARC | Extern | [5 empty] | RESTART | SHUTDOWN | CFG_REDUNDANT
Hardware | Enasys | IPU | MCU | ErrorIRQ | 3 | 0x40 | X | 2 | 0x40X203 | ERROR_CODES::IPU::vDCDC::MCU | TEMP_TRIP_MCU | Temp Trip Board | SHARC | Extern | [5 empty] | RESTART | SHUTDOWN | CFG_REDUNDANT
Hardware | Enasys | IPU | MCU | ErrorIRQ | 4 | 0x40 | X | 2 | 0x40X204 | ERROR_CODES::IPU::vDCDC::MCU | TEMP_TRIP_C1 | Temp Trip Choke 1 | SHARC | Extern | [5 empty] | RESTART | SHUTDOWN | CFG_REDUNDANT
Hardware | Enasys | IPU | MCU | ErrorIRQ | 5 | 0x40 | X | 2 | 0x40X205 | ERROR_CODES::IPU::vDCDC::MCU | TEMP_TRIP_C2 | Temp Trip Choke 2 | SHARC | Extern | [5 empty] | RESTART | SHUTDOWN | CFG_REDUNDANT
Hardware | Enasys | IPU | MCU | ErrorIRQ | 6 | 0x40 | X | 2 | 0x40X206 | ERROR_CODES::IPU::vDCDC::MCU | TEMP_TRIP_C3 | Temp Trip Choke 3 | SHARC | Extern | [5 empty] | RESTART | SHUTDOWN | CFG_REDUNDANT
Hardware | Enasys | IPU | MCU | ErrorIRQ | 7 | 0x40 | X | 2 | 0x40X207 | ERROR_CODES::IPU::vDCDC::MCU | DESAT_TRIP_1 | IGBT A Error | SHARC | Extern | [6 empty] | SHUTDOWN | CFG_REDUNDANT
Hardware | Enasys | IPU | MCU | ErrorIRQ | 8 | 0x40 | X | 2 | 0x40X208 | ERROR_CODES::IPU::vDCDC::MCU | DESAT_TRIP_2 | IGBT B Error | SHARC | Extern | [6 empty] | SHUTDOWN | CFG_REDUNDANT
Hardware | Enasys | IPU | MCU | ErrorIRQ | 9 | 0x40 | X | 2 | 0x40X209 | ERROR_CODES::IPU::vDCDC::MCU | DESAT_TRIP_3 | IGBT C Error | SHARC | Extern | [6 empty] | SHUTDOWN | CFG_REDUNDANT
Hardware | Enasys | IPU | MCU | ErrorIRQ | 10 | 0x40 | X | 2 | 0x40X20A | ERROR_CODES::IPU::vDCDC::MCU | INTERN_TRIP_1 | Modulation Error P1 | SHARC | Extern | [5 empty] | RESTART | SHUTDOWN | CFG_REDUNDANT
Hardware | Enasys | IPU | MCU | ErrorIRQ | 11 | 0x40 | X | 2 | 0x40X20B | ERROR_CODES::IPU::vDCDC::MCU | INTERN_TRIP_2 | Modulation Error P2 | SHARC | Extern | [5 empty] | RESTART | SHUTDOWN | CFG_REDUNDANT
Hardware | Enasys | IPU | MCU | ErrorIRQ | 12 | 0x40 | X | 2 | 0x40X20C | ERROR_CODES::IPU::vDCDC::MCU | INTERN_TRIP_3 | Modulation Error P3 | SHARC | Extern | [5 empty] | RESTART | SHUTDOWN | CFG_REDUNDANT
Hardware | Enasys | IPU | MCU | ErrorIRQ | 13 | 0x40 | X | 2 | 0x40X20D | ERROR_CODES::IPU::vDCDC::MCU | POWER_TRIP | Power Trip | SHARC | Extern | [6 empty] | SHUTDOWN | CFG_REDUNDANT
Hardware | Enasys | IPU | MCU | ErrorIRQ | 14 | 0x40 | X | 2 | 0x40X20E | ERROR_CODES::IPU::vDCDC::MCU | OC_TRIP_1 | Overcurrent Protection Phase A | SHARC | Extern | [5 empty] | RESTART | SHUTDOWN | CFG_REDUNDANT | Comparator@+-140Apk
Hardware | Enasys | IPU | MCU | ErrorIRQ | 15 | 0x40 | X | 2 | 0x40X20F | ERROR_CODES::IPU::vDCDC::MCU | OC_TRIP_2 | Overcurrent Protection Phase B | SHARC | Extern | [5 empty] | RESTART | SHUTDOWN | CFG_REDUNDANT | Comparator@+-140Apk
Hardware | Enasys | IPU | MCU | ErrorIRQ | 16 | 0x40 | X | 2 | 0x40X210 | ERROR_CODES::IPU::vDCDC::MCU | OC_TRIP_3 | Overcurrent Protection Phase C | SHARC | Extern | [5 empty] | RESTART | SHUTDOWN | CFG_REDUNDANT | Comparator@+-140Apk
Hardware | Enasys | IPU | MCU | ErrorIRQ | 17 | 0x40 | X | 2 | 0x40X211 | ERROR_CODES::IPU::vDCDC::MCU | SWFREQ_TRIP | Switching Frequency Error | SHARC | Extern | [5 empty] | RESTART | SHUTDOWN | CFG_REDUNDANT
Hardware | Enasys | IPU | MCU | ErrorIRQ | 18 | 0x40 | X | 2 | 0x40X212 | ERROR_CODES::IPU::vDCDC::MCU | RMS_TRIP | RMS Current Error | SHARC | Extern | [5 empty] | RESTART | SHUTDOWN | CFG_REDUNDANT
Hardware | Enasys | IPU | MCU | ErrorIRQ | 19 | 0x40 | X | 2 | 0x40X213 | ERROR_CODES::IPU::vDCDC::MCU | SOFTWARE_TRIP | Software Error | SHARC | Extern | [5 empty] | RESTART | SHUTDOWN | CFG_REDUNDANT
Hardware | Enasys | IPU | MCU | ErrorIRQ | 20 | 0x40 | X | 2 | 0x40X214 | ERROR_CODES::IPU::vDCDC::MCU | V1_TRIP | Bit 20 | SHARC | Extern | [5 empty] | RESTART | SHUTDOWN | CFG_REDUNDANT
Hardware | Enasys | IPU | MCU | ErrorIRQ | 21 | 0x40 | X | 2 | 0x40X215 | ERROR_CODES::IPU::vDCDC::MCU | V2_TRIP | Bit 21 | SHARC | Extern | [5 empty] | RESTART | SHUTDOWN | CFG_REDUNDANT
Hardware | Enasys | IPU | MCU | ErrorIRQ | 22 | 0x40 | X | 2 | 0x40X216 | ERROR_CODES::IPU::vDCDC::MCU | V3_TRIP | Bit 22 | SHARC | Extern | [5 empty] | RESTART | SHUTDOWN | CFG_REDUNDANT
Hardware | Enasys | IPU | MCU | ErrorIRQ | 23 | 0x40 | X | 2 | 0x40X217 | ERROR_CODES::IPU::vDCDC::MCU | V24_TRIP | 24 V Fault | SHARC | Extern | [5 empty] | RESTART | SHUTDOWN | CFG_REDUNDANT
Hardware | Enasys | IPU | MCU | ErrorIRQ | 24 | 0x40 | X | 2 | 0x40X218 | ERROR_CODES::IPU::vDCDC::MCU | OCA_TRIP | Overcurrent Phase A | SHARC | Extern | [5 empty] | RESTART | SHUTDOWN | CFG_REDUNDANT
Hardware | Enasys | IPU | MCU | ErrorIRQ | 25 | 0x40 | X | 2 | 0x40X219 | ERROR_CODES::IPU::vDCDC::MCU | OCB_TRIP | Overcurrent Phase B | SHARC | Extern | [5 empty] | RESTART | SHUTDOWN | CFG_REDUNDANT
Hardware | Enasys | IPU | MCU | ErrorIRQ | 26 | 0x40 | X | 2 | 0x40X21A | ERROR_CODES::IPU::vDCDC::MCU | OCC_TRIP | Overcurrent Phase C | SHARC | Extern | [5 empty] | RESTART | SHUTDOWN | CFG_REDUNDANT
Hardware | Enasys | IPU | MCU | ErrorIRQ | 27 | 0x40 | X | 2 | 0x40X21B | ERROR_CODES::IPU::vDCDC::MCU | UB1_TRIP | DC String 1 Overvoltage | SHARC | Extern | [5 empty] | RESTART | SHUTDOWN | CFG_REDUNDANT
Hardware | Enasys | IPU | MCU | ErrorIRQ | 28 | 0x40 | X | 2 | 0x40X21C | ERROR_CODES::IPU::vDCDC::MCU | UB2_TRIP | DC String 2 Overvoltage | SHARC | Extern | [5 empty] | RESTART | SHUTDOWN | CFG_REDUNDANT | Todo 170831 Heo FW
Hardware | Enasys | IPU | MCU | ErrorIRQ | 29 | 0x40 | X | 2 | 0x40X21D | ERROR_CODES::IPU::vDCDC::MCU | UB3_TRIP | DC String 3 Overvoltage | SHARC | Extern | [5 empty] | RESTART | SHUTDOWN | CFG_REDUNDANT | Todo 170831 Heo FW
Hardware | Enasys | IPU | MCU | ErrorIRQ | 30 | 0x40 | X | 2 | 0x40X21E | ERROR_CODES::IPU::vDCDC::MCU | TACHO_TRIP | Fan Error | SHARC | Extern | [5 empty] | RESTART | SHUTDOWN | CFG_REDUNDANT | Todo 170831 Heo FW
Hardware | Enasys | IPU | MCU | ErrorIRQ | 31 | 0x40 | X | 2 | 0x40X21F | ERROR_CODES::IPU::vDCDC::MCU | UZK_TRIP | DC-Link Overvoltage Fault | SHARC | Extern | [5 empty] | RESTART | SHUTDOWN | CFG_REDUNDANT
DSC | Enasys | IPU | FPGA | ErrorIRQ | 0 | 0x40 | X | 1 | 0x40X100 | ERROR_CODES::IPU::vDCDC::COM | CURRENT_LOOP_TRIP | CurrentLoop Open | SHARC | Extern | [5 empty] | RESTART | FORCED | CFG_REDUNDANT
DSC | Enasys | IPU | FPGA | ErrorIRQ | 1 | 0x40 | X | 1 | 0x40X101 | ERROR_CODES::IPU::vDCDC::COM | WATCHDOG_TRIP | Watchdog Timeout | SHARC | Extern | [5 empty] | RESTART | SHUTDOWN | CFG_REDUNDANT
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 0 | 0x20 | X | 4 | 0x20X400 | ERROR_CODES::IPU::v3LV1::EXT1 | TEMP_TRIP_IGBT_1 | (XT) Temp Trip IGBT 1 | IPU690V | HIGH | 85 | 0 |  |  |  | RESTART | SHUTDOWN | CFG_REDUNDANT | in while Loop
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 1 | 0x20 | X | 4 | 0x20X401 | ERROR_CODES::IPU::v3LV1::EXT1 | TEMP_TRIP_IGBT_2 | (XT) Temp Trip IGBT 2 | IPU690V | HIGH | 85 | 0 |  |  |  | RESTART | SHUTDOWN | CFG_REDUNDANT | in while Loop
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 2 | 0x20 | X | 4 | 0x20X402 | ERROR_CODES::IPU::v3LV1::EXT1 | TEMP_TRIP_IGBT_3 | (XT) Temp Trip IGBT 3 | IPU690V | HIGH | 85 | 0 |  |  |  | RESTART | SHUTDOWN | CFG_REDUNDANT | in while Loop
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 3 | 0x20 | X | 4 | 0x20X403 | ERROR_CODES::IPU::v3LV1::EXT1 | TEMP_TRIP_FILTERCHOKE | (XT) Temp Trip Filter Choke | IPU690V | HIGH | 160 | 0 |  |  |  | RESTART | SHUTDOWN | CFG_REDUNDANT | in while Loop
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 4 | 0x20 | X | 4 | 0x20X404 | ERROR_CODES::IPU::v3LV1::EXT1 | TEMP_TRIP_GRIDCHOKE | (XT) Temp Trip Grid Choke | IPU690V | HIGH | 150 | 0 |  |  |  | RESTART | SHUTDOWN | CFG_REDUNDANT | in while Loop
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 5 | 0x20 | X | 4 | 0x20X405 | ERROR_CODES::IPU::v3LV1::EXT1 | OUTPUT_PEAK_TRIP_1 | (XT) Output Current Peak Trip Phase 1 | IPU690V | HIGH | 600 | 0 |  |  |  | RESTART | FORCED | CFG_REDUNDANT | in DataIRQ (type & timeout hardcoded)
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 6 | 0x20 | X | 4 | 0x20X406 | ERROR_CODES::IPU::v3LV1::EXT1 | OUTPUT_PEAK_TRIP_2 | (XT) Output Current Peak Trip Phase 2 | IPU690V | HIGH | 600 | 0 |  |  |  | RESTART | FORCED | CFG_REDUNDANT | in DataIRQ (type & timeout hardcoded)
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 7 | 0x20 | X | 4 | 0x20X407 | ERROR_CODES::IPU::v3LV1::EXT1 | OUTPUT_PEAK_TRIP_3 | (XT) Output Current Peak Trip Phase 3 | IPU690V | HIGH | 600 | 0 |  |  |  | RESTART | FORCED | CFG_REDUNDANT | in DataIRQ (type & timeout hardcoded)
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 8 | 0x20 | X | 4 | 0x20X408 | ERROR_CODES::IPU::v3LV1::EXT1 | MODULE_PEAK_TRIP_1 | (XT) Module Current Peak Trip Phase 1 | IPU690V | HIGH | 420 | 0 |  |  |  | RESTART | FORCED | CFG_REDUNDANT | in DataIRQ (type & timeout hardcoded)
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 9 | 0x20 | X | 4 | 0x20X409 | ERROR_CODES::IPU::v3LV1::EXT1 | MODULE_PEAK_TRIP_2 | (XT) Module Current Peak Trip Phase 2 | IPU690V | HIGH | 420 | 0 |  |  |  | RESTART | FORCED | CFG_REDUNDANT | in DataIRQ (type & timeout hardcoded)
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 10 | 0x20 | X | 4 | 0x20X40A | ERROR_CODES::IPU::v3LV1::EXT1 | MODULE_PEAK_TRIP_3 | (XT) Module Current Peak Trip Phase 3 | IPU690V | HIGH | 420 | 0 |  |  |  | RESTART | FORCED | CFG_REDUNDANT | in DataIRQ (type & timeout hardcoded)
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 11 | 0x20 | X | 4 | 0x20X40B | ERROR_CODES::IPU::v3LV1::EXT1 | FILTER_RMS_TRIP_1 | (XT) Filter Current RMS Trip Phase 1 | IPU690V | HIGH | 42 | 0 |  |  |  | RESTART | SHUTDOWN | CFG_REDUNDANT | in DataIRQ (type & timeout hardcoded)
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 12 | 0x20 | X | 4 | 0x20X40C | ERROR_CODES::IPU::v3LV1::EXT1 | FILTER_RMS_TRIP_2 | (XT) Filter Current RMS Trip Phase 2 | IPU690V | HIGH | 42 | 0 |  |  |  | RESTART | SHUTDOWN | CFG_REDUNDANT | in DataIRQ (type & timeout hardcoded)
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 13 | 0x20 | X | 4 | 0x20X40D | ERROR_CODES::IPU::v3LV1::EXT1 | FILTER_RMS_TRIP_3 | (XT) Filter Current RMS Trip Phase 3 | IPU690V | HIGH | 42 | 0 |  |  |  | RESTART | SHUTDOWN | CFG_REDUNDANT | in DataIRQ (type & timeout hardcoded)
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 14 | 0x20 | X | 4 | 0x20X40E | ERROR_CODES::IPU::v3LV1::EXT1 | FILTER_SLOWRMS_TRIP_1 | (XT) Filter Current Slow RMS Trip Phase 1 | IPU690V | HIGH | 28 | 0 |  |  |  | RESTART | SHUTDOWN | CFG_REDUNDANT | in DataIRQ (type & timeout hardcoded)
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 15 | 0x20 | X | 4 | 0x20X40F | ERROR_CODES::IPU::v3LV1::EXT1 | FILTER_SLOWRMS_TRIP_2 | (XT) Filter Current Slow RMS Trip Phase 2 | IPU690V | HIGH | 28 | 0 |  |  |  | RESTART | SHUTDOWN | CFG_REDUNDANT | in DataIRQ (type & timeout hardcoded)
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 16 | 0x20 | X | 4 | 0x20X410 | ERROR_CODES::IPU::v3LV1::EXT1 | FILTER_SLOWRMS_TRIP_3 | (XT) Filter Current Slow RMS Trip Phase 3 | IPU690V | HIGH | 28 | 0 |  |  |  | RESTART | SHUTDOWN | CFG_REDUNDANT | in DataIRQ (type & timeout hardcoded)
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 17 | 0x20 | X | 4 | 0x20X411 | ERROR_CODES::IPU::v3LV1::EXT1 | OUTPUT_RMS_TRIP_1 | (XT) Output Current RMS Trip Phase 1 | IPU690V | HIGH | 145 | 0 |  |  |  | RESTART | SHUTDOWN | CFG_REDUNDANT | in checkMeasurements() [200 ms]
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 18 | 0x20 | X | 4 | 0x20X412 | ERROR_CODES::IPU::v3LV1::EXT1 | OUTPUT_RMS_TRIP_2 | (XT) Output Current RMS Trip Phase 2 | IPU690V | HIGH | 145 | 0 |  |  |  | RESTART | SHUTDOWN | CFG_REDUNDANT | in checkMeasurements() [200 ms]
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 19 | 0x20 | X | 4 | 0x20X413 | ERROR_CODES::IPU::v3LV1::EXT1 | OUTPUT_RMS_TRIP_3 | (XT) Output Current RMS Trip Phase 3 | IPU690V | HIGH | 145 | 0 |  |  |  | RESTART | SHUTDOWN | CFG_REDUNDANT | in checkMeasurements() [200 ms]
Grid | Enasys | IPU | Sharc | IPU3LInspector | 20 | 0x20 | X | 4 | 0x20X414 | ERROR_CODES::IPU::v3LV1::EXT1 | MODULE_FRD_FILTER_C | (XT) Fast Resonance Detection (FRD-F) | IPU690V | BOOL |  | 0 |  |  |  | AUTOACK | WARNING | CFG_REDUNDANT | not implemented
Grid | Enasys | IPU | Sharc | IPU3LInspector | 21 | 0x20 | X | 4 | 0x20X415 | ERROR_CODES::IPU::v3LV1::EXT1 | MODULE_FRD_OUTPUTPEAK | (XT) Fast Resonance Detection (FRD-P) | IPU690V | BOOL |  | 0 |  |  |  | AUTOACK | WARNING | CFG_REDUNDANT | not implemented
[5 empty] | 22 | 0x20 | X | 4 | 0x20X416 | ERROR_CODES::IPU::v3LV1::EXT1 | SIA_RUNNING | (XT) System Identification Algorithm (SIA) running... | IPU690V | BOOL |  | 0 |  |  |  | AUTOACK | WARNING | CFG_REDUNDANT | not implemented
[5 empty] | 23 | 0x20 | X | 4 | 0x20X417 | ERROR_CODES::IPU::v3LV1::EXT1 | SIA_WARNING | (XT) SIA Warning | IPU690V | BOOL |  | 0 |  |  |  | AUTOACK | WARNING | CFG_REDUNDANT | not implemented
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 24 | 0x20 | X | 4 | 0x20X418 | ERROR_CODES::IPU::v3LV1::EXT1 | NEUTRAL_RMS_TRIP | (XT) Neutral Current RMS Trip | IPU690V | HIGH | I_NEUTRAL | 5 |  |  |  | RESTART | SHUTDOWN | CFG_REDUNDANT
[5 empty] | 25 | 0x20 | X | 4 | 0x20X419 | ERROR_CODES::IPU::v3LV1::EXT1 | SUSPECT_HARMONICS_DETECTED | (XT) Suspect Harmonics marked | IPU690V | BOOL |  | 0 |  |  |  | AUTOACK | WARNING | CFG_REDUNDANT | not implemented
[5 empty] | 26 | 0x20 | X | 4 | 0x20X41A | ERROR_CODES::IPU::v3LV1::EXT1 | CRITICAL_HARMONICS_DETECTED | (XT) Compensation of critical harmonics blocked | IPU690V | BOOL |  | 0 |  |  |  | AUTOACK | WARNING | CFG_REDUNDANT | not implemented
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 0 | 0x20 | X | 8 | 0x20X800 | ERROR_CODES::IPU::v3LV1::EXT2 | UDC_P_TRIP | (XT) DC-Link Positive Voltage Fault | IPU690V | HIGH | 740 | 0 |  |  |  | RESTART | FORCED | CFG_REDUNDANT | in DataIRQ (type & timeout hardcoded)
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 1 | 0x20 | X | 8 | 0x20X801 | ERROR_CODES::IPU::v3LV1::EXT2 | UDC_N_TRIP | (XT) DC-Link Negative Voltage Fault | IPU690V | HIGH | 740 | 0 |  |  |  | RESTART | FORCED | CFG_REDUNDANT | in DataIRQ (type & timeout hardcoded)
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 2 | 0x20 | X | 8 | 0x20X802 | ERROR_CODES::IPU::v3LV1::EXT2 | UDC_DIFF_TRIP | (XT) DC-Link Voltage Imbalance | IPU690V | HIGH | 100 | 0 |  |  |  | RESTART | FORCED | CFG_GROUP | not implemented
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 3 | 0x20 | X | 8 | 0x20X803 | ERROR_CODES::IPU::v3LV1::EXT2 | UDC_P_PRECHG_TRIP | (XT) DC-Link Precharge Positive Voltage Trip | IPU690V | LOW | 180 | 0 |  |  |  |  | DISABLED | SINGLE | not implemented
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 4 | 0x20 | X | 8 | 0x20X804 | ERROR_CODES::IPU::v3LV1::EXT2 | UDC_N_PRECHG_TRIP | (XT) DC-Link Precharge Negative Voltage Trip | IPU690V | LOW | 180 | 0 |  |  |  |  | DISABLED | SINGLE | not implemented
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 5 | 0x20 | X | 8 | 0x20X805 | ERROR_CODES::IPU::v3LV1::EXT2 | UDC_P_PRECHG_5_TRIP | (XT) DC-Link Precharge Positive Undervoltage Trip | IPU690V | LOW | 165 | 0 |  |  |  |  | DISABLED | SINGLE | not implemented
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 6 | 0x20 | X | 8 | 0x20X806 | ERROR_CODES::IPU::v3LV1::EXT2 | UDC_N_PRECHG_5_TRIP | (XT) DC-Link Precharge Negative Undervoltage Trip | IPU690V | LOW | 165 | 0 |  |  |  |  | DISABLED | SINGLE | not implemented
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 7 | 0x20 | X | 8 | 0x20X807 | ERROR_CODES::IPU::v3LV1::EXT2 | UDC_P_PRECHG_MAX_TRIP | (XT) DC-Link Precharge Positive Overvoltage Trip | IPU690V | HIGH | 650 | 0 |  |  |  |  | DISABLED | SINGLE | not implemented
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 8 | 0x20 | X | 8 | 0x20X808 | ERROR_CODES::IPU::v3LV1::EXT2 | UDC_N_PRECHG_MAX_TRIP | (XT) DC-Link Precharge Negative Overvoltage Trip | IPU690V | HIGH | 650 | 0 |  |  |  |  | DISABLED | SINGLE | not implemented
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 0 | 0x20 | X | 4 | 0x20X400 | ERROR_CODES::IPU::v3LV1::EXT1 | TEMP_TRIP_IGBT_1 | (XT) Temp Trip IGBT 1 | IPUCompact4L | HIGH | 103 | 0 |  |  |  | RESTART | SHUTDOWN | CFG_REDUNDANT | in while Loop
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 1 | 0x20 | X | 4 | 0x20X401 | ERROR_CODES::IPU::v3LV1::EXT1 | TEMP_TRIP_IGBT_2 | (XT) Temp Trip IGBT 2 | IPUCompact4L | HIGH | 103 | 0 |  |  |  | RESTART | SHUTDOWN | CFG_REDUNDANT | in while Loop
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 2 | 0x20 | X | 4 | 0x20X402 | ERROR_CODES::IPU::v3LV1::EXT1 | TEMP_TRIP_IGBT_3 | (XT) Temp Trip IGBT 3 | IPUCompact4L | HIGH | 103 | 0 |  |  |  | RESTART | SHUTDOWN | CFG_REDUNDANT | in while Loop
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 3 | 0x20 | X | 4 | 0x20X403 | ERROR_CODES::IPU::v3LV1::EXT1 | TEMP_TRIP_FILTERCHOKE | (XT) Temp Trip Filter Choke | IPUCompact4L | HIGH | 150 | 0 |  |  |  | RESTART | SHUTDOWN | CFG_REDUNDANT | in while Loop
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 4 | 0x20 | X | 4 | 0x20X404 | ERROR_CODES::IPU::v3LV1::EXT1 | TEMP_TRIP_GRIDCHOKE | (XT) Temp Trip Grid Choke | IPUCompact4L | HIGH | 150 | 0 |  |  |  | RESTART | SHUTDOWN | CFG_REDUNDANT | in while Loop
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 5 | 0x20 | X | 4 | 0x20X405 | ERROR_CODES::IPU::v3LV1::EXT1 | OUTPUT_PEAK_TRIP_1 | (XT) Output Current Peak Trip Phase 1 | IPUCompact4L | HIGH | 180 | 0 |  |  |  | RESTART | FORCED | CFG_REDUNDANT | in DataIRQ (type & timeout hardcoded)
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 6 | 0x20 | X | 4 | 0x20X406 | ERROR_CODES::IPU::v3LV1::EXT1 | OUTPUT_PEAK_TRIP_2 | (XT) Output Current Peak Trip Phase 2 | IPUCompact4L | HIGH | 180 | 0 |  |  |  | RESTART | FORCED | CFG_REDUNDANT | in DataIRQ (type & timeout hardcoded)
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 7 | 0x20 | X | 4 | 0x20X407 | ERROR_CODES::IPU::v3LV1::EXT1 | OUTPUT_PEAK_TRIP_3 | (XT) Output Current Peak Trip Phase 3 | IPUCompact4L | HIGH | 180 | 0 |  |  |  | RESTART | FORCED | CFG_REDUNDANT | in DataIRQ (type & timeout hardcoded)
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 8 | 0x20 | X | 4 | 0x20X408 | ERROR_CODES::IPU::v3LV1::EXT1 | MODULE_PEAK_TRIP_1 | (XT) Module Current Peak Trip Phase 1 | IPUCompact4L | HIGH | 180 | 0 |  |  |  | RESTART | FORCED | CFG_REDUNDANT | in DataIRQ (type & timeout hardcoded)
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 9 | 0x20 | X | 4 | 0x20X409 | ERROR_CODES::IPU::v3LV1::EXT1 | MODULE_PEAK_TRIP_2 | (XT) Module Current Peak Trip Phase 2 | IPUCompact4L | HIGH | 180 | 0 |  |  |  | RESTART | FORCED | CFG_REDUNDANT | in DataIRQ (type & timeout hardcoded)
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 10 | 0x20 | X | 4 | 0x20X40A | ERROR_CODES::IPU::v3LV1::EXT1 | MODULE_PEAK_TRIP_3 | (XT) Module Current Peak Trip Phase 3 | IPUCompact4L | HIGH | 180 | 0 |  |  |  | RESTART | FORCED | CFG_REDUNDANT | in DataIRQ (type & timeout hardcoded)
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 11 | 0x20 | X | 4 | 0x20X40B | ERROR_CODES::IPU::v3LV1::EXT1 | FILTER_RMS_TRIP_1 | (XT) Filter Current RMS Trip Phase 1 | IPUCompact4L | HIGH | 28 | 0 |  |  |  | RESTART | SHUTDOWN | CFG_REDUNDANT | in DataIRQ (type & timeout hardcoded)
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 12 | 0x20 | X | 4 | 0x20X40C | ERROR_CODES::IPU::v3LV1::EXT1 | FILTER_RMS_TRIP_2 | (XT) Filter Current RMS Trip Phase 2 | IPUCompact4L | HIGH | 28 | 0 |  |  |  | RESTART | SHUTDOWN | CFG_REDUNDANT | in DataIRQ (type & timeout hardcoded)
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 13 | 0x20 | X | 4 | 0x20X40D | ERROR_CODES::IPU::v3LV1::EXT1 | FILTER_RMS_TRIP_3 | (XT) Filter Current RMS Trip Phase 3 | IPUCompact4L | HIGH | 28 | 0 |  |  |  | RESTART | SHUTDOWN | CFG_REDUNDANT | in DataIRQ (type & timeout hardcoded)
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 14 | 0x20 | X | 4 | 0x20X40E | ERROR_CODES::IPU::v3LV1::EXT1 | FILTER_SLOWRMS_TRIP_1 | (XT) Filter Current Slow RMS Trip Phase 1 | IPUCompact4L | HIGH | 20 | 0 |  |  |  | RESTART | SHUTDOWN | CFG_REDUNDANT | in DataIRQ (type & timeout hardcoded)
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 15 | 0x20 | X | 4 | 0x20X40F | ERROR_CODES::IPU::v3LV1::EXT1 | FILTER_SLOWRMS_TRIP_2 | (XT) Filter Current Slow RMS Trip Phase 2 | IPUCompact4L | HIGH | 20 | 0 |  |  |  | RESTART | SHUTDOWN | CFG_REDUNDANT | in DataIRQ (type & timeout hardcoded)
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 16 | 0x20 | X | 4 | 0x20X410 | ERROR_CODES::IPU::v3LV1::EXT1 | FILTER_SLOWRMS_TRIP_3 | (XT) Filter Current Slow RMS Trip Phase 3 | IPUCompact4L | HIGH | 20 | 0 |  |  |  | RESTART | SHUTDOWN | CFG_REDUNDANT | in DataIRQ (type & timeout hardcoded)
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 17 | 0x20 | X | 4 | 0x20X411 | ERROR_CODES::IPU::v3LV1::EXT1 | OUTPUT_RMS_TRIP_1 | (XT) Output Current RMS Trip Phase 1 | IPUCompact4L | HIGH | 75 | 0 |  |  |  | RESTART | SHUTDOWN | CFG_REDUNDANT | in checkMeasurements() [200 ms]
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 18 | 0x20 | X | 4 | 0x20X412 | ERROR_CODES::IPU::v3LV1::EXT1 | OUTPUT_RMS_TRIP_2 | (XT) Output Current RMS Trip Phase 2 | IPUCompact4L | HIGH | 75 | 0 |  |  |  | RESTART | SHUTDOWN | CFG_REDUNDANT | in checkMeasurements() [200 ms]
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 19 | 0x20 | X | 4 | 0x20X413 | ERROR_CODES::IPU::v3LV1::EXT1 | OUTPUT_RMS_TRIP_3 | (XT) Output Current RMS Trip Phase 3 | IPUCompact4L | HIGH | 75 | 0 |  |  |  | RESTART | SHUTDOWN | CFG_REDUNDANT | in checkMeasurements() [200 ms]
Grid | Enasys | IPU | Sharc | IPU3LInspector | 20 | 0x20 | X | 4 | 0x20X414 | ERROR_CODES::IPU::v3LV1::EXT1 | MODULE_FRD_FILTER_C | (XT) Fast Resonance Detection (FRD-F) | IPUCompact4L | BOOL |  | 0 |  |  |  | AUTOACK | WARNING | CFG_REDUNDANT | not implemented
Grid | Enasys | IPU | Sharc | IPU3LInspector | 21 | 0x20 | X | 4 | 0x20X415 | ERROR_CODES::IPU::v3LV1::EXT1 | MODULE_FRD_OUTPUTPEAK | (XT) Fast Resonance Detection (FRD-P) | IPUCompact4L | BOOL |  | 0 |  |  |  | AUTOACK | WARNING | CFG_REDUNDANT | not implemented
[5 empty] | 22 | 0x20 | X | 4 | 0x20X416 | ERROR_CODES::IPU::v3LV1::EXT1 | SIA_RUNNING | (XT) System Identification Algorithm (SIA) running... | IPUCompact4L | BOOL |  | 0 |  |  |  | AUTOACK | WARNING | CFG_REDUNDANT | not implemented
[5 empty] | 23 | 0x20 | X | 4 | 0x20X417 | ERROR_CODES::IPU::v3LV1::EXT1 | SIA_WARNING | (XT) SIA Warning | IPUCompact4L | BOOL |  | 0 |  |  |  | AUTOACK | WARNING | CFG_REDUNDANT | not implemented
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 24 | 0x20 | X | 4 | 0x20X418 | ERROR_CODES::IPU::v3LV1::EXT1 | NEUTRAL_RMS_TRIP | (XT) Neutral Current RMS Trip | IPUCompact4L | HIGH | I_NEUTRAL | 5 |  |  |  | RESTART | SHUTDOWN | CFG_REDUNDANT
[5 empty] | 25 | 0x20 | X | 4 | 0x20X419 | ERROR_CODES::IPU::v3LV1::EXT1 | SUSPECT_HARMONICS_DETECTED | (XT) Suspect Harmonics marked | IPUCompact4L | BOOL |  | 0 |  |  |  | AUTOACK | WARNING | CFG_REDUNDANT | not implemented
[5 empty] | 26 | 0x20 | X | 4 | 0x20X41A | ERROR_CODES::IPU::v3LV1::EXT1 | CRITICAL_HARMONICS_DETECTED | (XT) Compensation of critical harmonics blocked | IPUCompact4L | BOOL |  | 0 |  |  |  | AUTOACK | WARNING | CFG_REDUNDANT | not implemented
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 0 | 0x20 | X | 8 | 0x20X800 | ERROR_CODES::IPU::v3LV1::EXT2 | UDC_P_TRIP | (XT) DC-Link Positive Voltage Fault | IPUCompact4L | HIGH | 435 | 0 |  |  |  | RESTART | FORCED | CFG_REDUNDANT | in DataIRQ (type & timeout hardcoded)
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 1 | 0x20 | X | 8 | 0x20X801 | ERROR_CODES::IPU::v3LV1::EXT2 | UDC_N_TRIP | (XT) DC-Link Negative Voltage Fault | IPUCompact4L | HIGH | 435 | 0 |  |  |  | RESTART | FORCED | CFG_REDUNDANT | in DataIRQ (type & timeout hardcoded)
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 2 | 0x20 | X | 8 | 0x20X802 | ERROR_CODES::IPU::v3LV1::EXT2 | UDC_DIFF_TRIP | (XT) DC-Link Voltage Imbalance | IPUCompact4L | HIGH | 60 | 0 |  |  |  | RESTART | FORCED | SINGLE | not implemented
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 3 | 0x20 | X | 8 | 0x20X803 | ERROR_CODES::IPU::v3LV1::EXT2 | UDC_P_PRECHG_TRIP | (XT) DC-Link Precharge Positive Voltage Trip | IPUCompact4L | LOW | 180 | 0 |  |  |  |  | DISABLED | SINGLE | not implemented
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 4 | 0x20 | X | 8 | 0x20X804 | ERROR_CODES::IPU::v3LV1::EXT2 | UDC_N_PRECHG_TRIP | (XT) DC-Link Precharge Negative Voltage Trip | IPUCompact4L | LOW | 180 | 0 |  |  |  |  | DISABLED | SINGLE | not implemented
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 5 | 0x20 | X | 8 | 0x20X805 | ERROR_CODES::IPU::v3LV1::EXT2 | UDC_P_PRECHG_5_TRIP | (XT) DC-Link Precharge Positive Undervoltage Trip | IPUCompact4L | LOW | 165 | 0 |  |  |  |  | DISABLED | SINGLE | not implemented
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 6 | 0x20 | X | 8 | 0x20X806 | ERROR_CODES::IPU::v3LV1::EXT2 | UDC_N_PRECHG_5_TRIP | (XT) DC-Link Precharge Negative Undervoltage Trip | IPUCompact4L | LOW | 165 | 0 |  |  |  |  | DISABLED | SINGLE | not implemented
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 7 | 0x20 | X | 8 | 0x20X807 | ERROR_CODES::IPU::v3LV1::EXT2 | UDC_P_PRECHG_MAX_TRIP | (XT) DC-Link Precharge Positive Overvoltage Trip | IPUCompact4L | HIGH | 430 | 0 |  |  |  |  | DISABLED | SINGLE | not implemented
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 8 | 0x20 | X | 8 | 0x20X808 | ERROR_CODES::IPU::v3LV1::EXT2 | UDC_N_PRECHG_MAX_TRIP | (XT) DC-Link Precharge Negative Overvoltage Trip | IPUCompact4L | HIGH | 430 | 0 |  |  |  |  | DISABLED | SINGLE | not implemented
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 0 | 0x20 | X | 4 | 0x20X400 | ERROR_CODES::IPU::v3LV1::EXT1 | TEMP_TRIP_IGBT_1 | (XT) Temp Trip IGBT 1 | IPULab | HIGH | 109 | 7 |  |  |  | RESTART | SHUTDOWN | CFG_REDUNDANT | in while Loop
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 1 | 0x20 | X | 4 | 0x20X401 | ERROR_CODES::IPU::v3LV1::EXT1 | TEMP_TRIP_IGBT_2 | (XT) Temp Trip IGBT 2 | IPULab | HIGH | 109 | 7 |  |  |  | RESTART | SHUTDOWN | CFG_REDUNDANT | in while Loop
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 2 | 0x20 | X | 4 | 0x20X402 | ERROR_CODES::IPU::v3LV1::EXT1 | TEMP_TRIP_IGBT_3 | (XT) Temp Trip IGBT 3 | IPULab | HIGH | 109 | 7 |  |  |  | RESTART | SHUTDOWN | CFG_REDUNDANT | in while Loop
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 3 | 0x20 | X | 4 | 0x20X403 | ERROR_CODES::IPU::v3LV1::EXT1 | TEMP_TRIP_FILTERCHOKE | (XT) Temp Trip Filter Choke | IPULab | HIGH | 170 | 7 |  |  |  | RESTART | SHUTDOWN | CFG_REDUNDANT | in while Loop
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 4 | 0x20 | X | 4 | 0x20X404 | ERROR_CODES::IPU::v3LV1::EXT1 | TEMP_TRIP_GRIDCHOKE | (XT) Temp Trip Grid Choke | IPULab | HIGH | 170 | 7 |  |  |  | RESTART | SHUTDOWN | CFG_REDUNDANT | in while Loop
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 5 | 0x20 | X | 4 | 0x20X405 | ERROR_CODES::IPU::v3LV1::EXT1 | OUTPUT_PEAK_TRIP_1 | (XT) Output Current Peak Trip Phase 1 | IPULab | HIGH | 30 | 0 |  |  |  | RESTART | FORCED | CFG_REDUNDANT | in DataIRQ (type & timeout hardcoded)
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 6 | 0x20 | X | 4 | 0x20X406 | ERROR_CODES::IPU::v3LV1::EXT1 | OUTPUT_PEAK_TRIP_2 | (XT) Output Current Peak Trip Phase 2 | IPULab | HIGH | 30 | 0 |  |  |  | RESTART | FORCED | CFG_REDUNDANT | in DataIRQ (type & timeout hardcoded)
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 7 | 0x20 | X | 4 | 0x20X407 | ERROR_CODES::IPU::v3LV1::EXT1 | OUTPUT_PEAK_TRIP_3 | (XT) Output Current Peak Trip Phase 3 | IPULab | HIGH | 30 | 0 |  |  |  | RESTART | FORCED | CFG_REDUNDANT | in DataIRQ (type & timeout hardcoded)
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 8 | 0x20 | X | 4 | 0x20X408 | ERROR_CODES::IPU::v3LV1::EXT1 | MODULE_PEAK_TRIP_1 | (XT) Module Current Peak Trip Phase 1 | IPULab | HIGH | 30 | 0 |  |  |  | RESTART | FORCED | CFG_REDUNDANT | in DataIRQ (type & timeout hardcoded)
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 9 | 0x20 | X | 4 | 0x20X409 | ERROR_CODES::IPU::v3LV1::EXT1 | MODULE_PEAK_TRIP_2 | (XT) Module Current Peak Trip Phase 2 | IPULab | HIGH | 30 | 0 |  |  |  | RESTART | FORCED | CFG_REDUNDANT | in DataIRQ (type & timeout hardcoded)
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 10 | 0x20 | X | 4 | 0x20X40A | ERROR_CODES::IPU::v3LV1::EXT1 | MODULE_PEAK_TRIP_3 | (XT) Module Current Peak Trip Phase 3 | IPULab | HIGH | 30 | 0 |  |  |  | RESTART | FORCED | CFG_REDUNDANT | in DataIRQ (type & timeout hardcoded)
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 11 | 0x20 | X | 4 | 0x20X40B | ERROR_CODES::IPU::v3LV1::EXT1 | FILTER_RMS_TRIP_1 | (XT) Filter Current RMS Trip Phase 1 | IPULab | HIGH | 8.5 | 0 |  |  |  | RESTART | SHUTDOWN | CFG_REDUNDANT | in DataIRQ (type & timeout hardcoded)
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 12 | 0x20 | X | 4 | 0x20X40C | ERROR_CODES::IPU::v3LV1::EXT1 | FILTER_RMS_TRIP_2 | (XT) Filter Current RMS Trip Phase 2 | IPULab | HIGH | 8.5 | 0 |  |  |  | RESTART | SHUTDOWN | CFG_REDUNDANT | in DataIRQ (type & timeout hardcoded)
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 13 | 0x20 | X | 4 | 0x20X40D | ERROR_CODES::IPU::v3LV1::EXT1 | FILTER_RMS_TRIP_3 | (XT) Filter Current RMS Trip Phase 3 | IPULab | HIGH | 8.5 | 0 |  |  |  | RESTART | SHUTDOWN | CFG_REDUNDANT | in DataIRQ (type & timeout hardcoded)
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 14 | 0x20 | X | 4 | 0x20X40E | ERROR_CODES::IPU::v3LV1::EXT1 | FILTER_SLOWRMS_TRIP_1 | (XT) Filter Current Slow RMS Trip Phase 1 | IPULab | HIGH | 8.0 | 0 |  |  |  | RESTART | SHUTDOWN | CFG_REDUNDANT | in DataIRQ (type & timeout hardcoded)
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 15 | 0x20 | X | 4 | 0x20X40F | ERROR_CODES::IPU::v3LV1::EXT1 | FILTER_SLOWRMS_TRIP_2 | (XT) Filter Current Slow RMS Trip Phase 2 | IPULab | HIGH | 8.0 | 0 |  |  |  | RESTART | SHUTDOWN | CFG_REDUNDANT | in DataIRQ (type & timeout hardcoded)
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 16 | 0x20 | X | 4 | 0x20X410 | ERROR_CODES::IPU::v3LV1::EXT1 | FILTER_SLOWRMS_TRIP_3 | (XT) Filter Current Slow RMS Trip Phase 3 | IPULab | HIGH | 8.0 | 0 |  |  |  | RESTART | SHUTDOWN | CFG_REDUNDANT | in DataIRQ (type & timeout hardcoded)
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 17 | 0x20 | X | 4 | 0x20X411 | ERROR_CODES::IPU::v3LV1::EXT1 | OUTPUT_RMS_TRIP_1 | (XT) Output Current RMS Trip Phase 1 | IPULab | HIGH | 16 | 7 |  |  |  | RESTART | SHUTDOWN | CFG_REDUNDANT | in checkMeasurements() [200 ms]
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 18 | 0x20 | X | 4 | 0x20X412 | ERROR_CODES::IPU::v3LV1::EXT1 | OUTPUT_RMS_TRIP_2 | (XT) Output Current RMS Trip Phase 2 | IPULab | HIGH | 16 | 7 |  |  |  | RESTART | SHUTDOWN | CFG_REDUNDANT | in checkMeasurements() [200 ms]
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 19 | 0x20 | X | 4 | 0x20X413 | ERROR_CODES::IPU::v3LV1::EXT1 | OUTPUT_RMS_TRIP_3 | (XT) Output Current RMS Trip Phase 3 | IPULab | HIGH | 16 | 7 |  |  |  | RESTART | SHUTDOWN | CFG_REDUNDANT | in checkMeasurements() [200 ms]
Grid | Enasys | IPU | Sharc | IPU3LInspector | 20 | 0x20 | X | 4 | 0x20X414 | ERROR_CODES::IPU::v3LV1::EXT1 | MODULE_FRD_FILTER_C | (XT) Fast Resonance Detection (FRD-F) | IPULab | BOOL |  | 0 |  |  |  | AUTOACK | WARNING | CFG_REDUNDANT | not implemented
Grid | Enasys | IPU | Sharc | IPU3LInspector | 21 | 0x20 | X | 4 | 0x20X415 | ERROR_CODES::IPU::v3LV1::EXT1 | MODULE_FRD_OUTPUTPEAK | (XT) Fast Resonance Detection (FRD-P) | IPULab | BOOL |  | 0 |  |  |  | AUTOACK | WARNING | CFG_REDUNDANT | not implemented
[5 empty] | 22 | 0x20 | X | 4 | 0x20X416 | ERROR_CODES::IPU::v3LV1::EXT1 | SIA_RUNNING | (XT) System Identification Algorithm (SIA) running... | IPULab | BOOL |  | 0 |  |  |  | AUTOACK | WARNING | CFG_REDUNDANT | not implemented
[5 empty] | 23 | 0x20 | X | 4 | 0x20X417 | ERROR_CODES::IPU::v3LV1::EXT1 | SIA_WARNING | (XT) SIA Warning | IPULab | BOOL |  | 0 |  |  |  | AUTOACK | WARNING | CFG_REDUNDANT | not implemented
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 24 | 0x20 | X | 4 | 0x20X418 | ERROR_CODES::IPU::v3LV1::EXT1 | NEUTRAL_RMS_TRIP | (XT) Neutral Current RMS Trip | IPULab | HIGH | I_NEUTRAL | 5 |  |  |  | RESTART | SHUTDOWN | CFG_REDUNDANT
[5 empty] | 25 | 0x20 | X | 4 | 0x20X419 | ERROR_CODES::IPU::v3LV1::EXT1 | SUSPECT_HARMONICS_DETECTED | (XT) Suspect Harmonics marked | IPULab | BOOL |  | 0 |  |  |  | AUTOACK | WARNING | CFG_REDUNDANT | not implemented
[5 empty] | 26 | 0x20 | X | 4 | 0x20X41A | ERROR_CODES::IPU::v3LV1::EXT1 | CRITICAL_HARMONICS_DETECTED | (XT) Compensation of critical harmonics blocked | IPULab | BOOL |  | 0 |  |  |  | AUTOACK | WARNING | CFG_REDUNDANT | not implemented
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 0 | 0x20 | X | 8 | 0x20X800 | ERROR_CODES::IPU::v3LV1::EXT2 | UDC_P_TRIP | (XT) DC-Link Positive Voltage Fault | IPULab | HIGH | 30 | 0 |  |  |  | RESTART | FORCED | CFG_REDUNDANT | in DataIRQ (type & timeout hardcoded)
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 1 | 0x20 | X | 8 | 0x20X801 | ERROR_CODES::IPU::v3LV1::EXT2 | UDC_N_TRIP | (XT) DC-Link Negative Voltage Fault | IPULab | HIGH | 30 | 0 |  |  |  | RESTART | FORCED | CFG_REDUNDANT | in DataIRQ (type & timeout hardcoded)
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 2 | 0x20 | X | 8 | 0x20X802 | ERROR_CODES::IPU::v3LV1::EXT2 | UDC_DIFF_TRIP | (XT) DC-Link Voltage Imbalance | IPULab | HIGH | 3 | 0 |  |  |  | RESTART | FORCED | CFG_GROUP | not implemented
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 3 | 0x20 | X | 8 | 0x20X803 | ERROR_CODES::IPU::v3LV1::EXT2 | UDC_P_PRECHG_TRIP | (XT) DC-Link Precharge Positive Voltage Trip | IPULab | LOW | 6 | 0 |  |  |  |  | DISABLED | SINGLE | not implemented
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 4 | 0x20 | X | 8 | 0x20X804 | ERROR_CODES::IPU::v3LV1::EXT2 | UDC_N_PRECHG_TRIP | (XT) DC-Link Precharge Negative Voltage Trip | IPULab | LOW | 6 | 0 |  |  |  |  | DISABLED | SINGLE | not implemented
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 5 | 0x20 | X | 8 | 0x20X805 | ERROR_CODES::IPU::v3LV1::EXT2 | UDC_P_PRECHG_5_TRIP | (XT) DC-Link Precharge Positive Undervoltage Trip | IPULab | LOW | 5.5 | 0 |  |  |  |  | DISABLED | SINGLE | not implemented
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 6 | 0x20 | X | 8 | 0x20X806 | ERROR_CODES::IPU::v3LV1::EXT2 | UDC_N_PRECHG_5_TRIP | (XT) DC-Link Precharge Negative Undervoltage Trip | IPULab | LOW | 5.5 | 0 |  |  |  |  | DISABLED | SINGLE | not implemented
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 7 | 0x20 | X | 8 | 0x20X807 | ERROR_CODES::IPU::v3LV1::EXT2 | UDC_P_PRECHG_MAX_TRIP | (XT) DC-Link Precharge Positive Overvoltage Trip | IPULab | HIGH | 23 | 0 |  |  |  |  | DISABLED | SINGLE | not implemented
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 8 | 0x20 | X | 8 | 0x20X808 | ERROR_CODES::IPU::v3LV1::EXT2 | UDC_N_PRECHG_MAX_TRIP | (XT) DC-Link Precharge Negative Overvoltage Trip | IPULab | HIGH | 23 | 0 |  |  |  |  | DISABLED | SINGLE | not implemented
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 9 | 0x20 | X | 8 | 0x20X809 | ERROR_CODES::IPU::v3LV1::EXT2 | HARDWARE_TRIP | (XT) Hardware Trip | SHARC | BOOL |  | 0 |  |  |  |  | SHUTDOWN | CFG_REDUNDANT | kein Acknowlege möglich laut Enasys
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 10 | 0x20 | X | 8 | 0x20X80A | ERROR_CODES::IPU::v3LV1::EXT2 | PRECHARGE_TRIP | (XT) Precharge Trip | SHARC | BOOL |  | 0 |  |  |  | RESTART | SHUTDOWN | CFG_REDUNDANT
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 11 | 0x20 | X | 8 | 0x20X80B | ERROR_CODES::IPU::v3LV1::EXT2 | STATE_TRIP | (XT) State Trip | SHARC | BOOL |  | 0 |  |  |  | RESTART | SHUTDOWN | CFG_REDUNDANT
Software | MR | Control | Sharc | IPU3LInspector | 12 | 0x20 | X | 8 | 0x20X80C | ERROR_CODES::IPU::v3LV1::EXT2 | TRH_ERROR | (XT) Transient Handling Error | SHARC | BOOL |  | 0 |  |  |  |  | SHUTDOWN | CFG_REDUNDANT
Software | MR | CCU Master | Sharc | IPU3LInspector | 13 | 0x20 | X | 8 | 0x20X80D | ERROR_CODES::IPU::v3LV1::EXT2 | M_TIMEOUT | (XT) Communication Timeout @ Master | SHARC | BOOL |  | 0 |  |  |  |  | DISABLED | CFG_REDUNDANT
Software | MR | CCU Slave | Sharc | IPU3LInspector | 14 | 0x20 | X | 8 | 0x20X80E | ERROR_CODES::IPU::v3LV1::EXT2 | S_COMMUNICATION | (XT) Communication Error @ Slave | SHARC | BOOL |  | 0 |  |  |  |  | DISABLED | CFG_REDUNDANT
Software | MR | CCU Slave | Sharc | IPU3LInspector | 15 | 0x20 | X | 8 | 0x20X80F | ERROR_CODES::IPU::v3LV1::EXT2 | S_SOFTWARE | (XT) SW Error @ Slave | SHARC | BOOL |  | 0 |  |  |  |  | DISABLED | CFG_REDUNDANT
Software | MR | StateMachine | Sharc | IPU3LInspector | 16 | 0x20 | X | 8 | 0x20X810 | ERROR_CODES::IPU::v3LV1::EXT2 | INDIVIDUAL_SM_TIMEOUT | (XT) IPU Statemachine timeout | SHARC | BOOL |  | 0 |  |  |  |  | SHUTDOWN | CFG_REDUNDANT
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 17 | 0x20 | X | 8 | 0x20X811 | ERROR_CODES::IPU::v3LV1::EXT2 | WRONGIPUTYPE | (XT) Incorrect IPU type detected | SHARC | BOOL |  | 0 |  |  |  |  | SHUTDOWN | CFG_REDUNDANT
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 18 | 0x20 | X | 8 | 0x20X812 | ERROR_CODES::IPU::v3LV1::EXT2 | WRONGFWVERSION | (XT) IPU Firmware incompatible | SHARC | BOOL |  | 0 |  |  |  |  | SHUTDOWN | CFG_REDUNDANT
Software | MR | StateMachine | Sharc | IPU3LInspector | 19 | 0x20 | X | 8 | 0x20X813 | ERROR_CODES::IPU::v3LV1::EXT2 | INDIV_SM_IGNORED_SYSLOCK | (XT) individual SM ignored Syslock | SHARC | BOOL |  | 0 |  |  |  |  | SHUTDOWN | CFG_REDUNDANT
|  |  | Sharc | IPU3LInspector | 20 | 0x20 | X | 8 | 0x20X814 | ERROR_CODES::IPU::v3LV1::EXT2 | ENABLE24_OFF | (XT) ENABLE 24V OFF | SHARC | BOOL |  | 0 |  |  |  |  | SHUTDOWN | CFG_REDUNDANT
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 0 | 0x40 | X | 4 | 0x40X400 | ERROR_CODES::IPU::vDCDC::EXT1 | TEMP_TRIP_IGBT | (XT) Temp Trip IGBT | IPUDCDC | HIGH | 105 | 0 |  |  |  | RESTART | SHUTDOWN | CFG_REDUNDANT
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 1 | 0x40 | X | 4 | 0x40X401 | ERROR_CODES::IPU::vDCDC::EXT1 | TEMP_CHOKE_TRIP_C | (XT) Temp Trip Choke C | IPUDCDC | HIGH | 130 | 0 |  |  |  | RESTART | SHUTDOWN | CFG_REDUNDANT
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 2 | 0x40 | X | 4 | 0x40X402 | ERROR_CODES::IPU::vDCDC::EXT1 | TEMP_CHOKE_TRIP_B | (XT) Temp Trip Choke B | IPUDCDC | HIGH | 130 | 0 |  |  |  | RESTART | SHUTDOWN | CFG_REDUNDANT
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 3 | 0x40 | X | 4 | 0x40X403 | ERROR_CODES::IPU::vDCDC::EXT1 | TEMP_CHOKE_TRIP_A | (XT) Temp Trip Choke A | IPUDCDC | HIGH | 130 | 0 |  |  |  | RESTART | SHUTDOWN | CFG_REDUNDANT
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 4 | 0x40 | X | 4 | 0x40X404 | ERROR_CODES::IPU::vDCDC::EXT1 | PEAK_CURRENT_TRIP_A | (XT) String Current Peak Trip Phase A | IPUDCDC | HIGH | 130 | 0 |  |  |  | RESTART | FORCED | CFG_REDUNDANT
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 5 | 0x40 | X | 4 | 0x40X405 | ERROR_CODES::IPU::vDCDC::EXT1 | PEAK_CURRENT_TRIP_B | (XT) String Current Peak Trip Phase B | IPUDCDC | HIGH | 130 | 0 |  |  |  | RESTART | FORCED | CFG_REDUNDANT
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 6 | 0x40 | X | 4 | 0x40X406 | ERROR_CODES::IPU::vDCDC::EXT1 | PEAK_CURRENT_TRIP_C | (XT) String Current Peak Trip Phase C | IPUDCDC | HIGH | 130 | 0 |  |  |  | RESTART | FORCED | CFG_REDUNDANT
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 7 | 0x40 | X | 4 | 0x40X407 | ERROR_CODES::IPU::vDCDC::EXT1 | STRING_HIGH_VOLTAGE_TRIP_A | (XT) String High Voltage Trip Phase A | IPUDCDC | HIGH | 850 | 0 |  |  |  | RESTART | FORCED | CFG_REDUNDANT
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 8 | 0x40 | X | 4 | 0x40X408 | ERROR_CODES::IPU::vDCDC::EXT1 | STRING_HIGH_VOLTAGE_TRIP_B | (XT) String High Voltage Trip Phase B | IPUDCDC | HIGH | 850 | 0 |  |  |  | RESTART | FORCED | CFG_REDUNDANT
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 9 | 0x40 | X | 4 | 0x40X409 | ERROR_CODES::IPU::vDCDC::EXT1 | STRING_HIGH_VOLTAGE_TRIP_C | (XT) String High Voltage Trip Phase C | IPUDCDC | HIGH | 850 | 0 |  |  |  | RESTART | FORCED | CFG_REDUNDANT
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 10 | 0x40 | X | 4 | 0x40X40A | ERROR_CODES::IPU::vDCDC::EXT1 | STRING_LOW_VOLTAGE_TRIP_A | (XT) String Low Voltage Trip Phase A | IPUDCDC | LOW | 200 | 0 |  |  |  | RESTART | FORCED | CFG_REDUNDANT
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 11 | 0x40 | X | 4 | 0x40X40B | ERROR_CODES::IPU::vDCDC::EXT1 | STRING_LOW_VOLTAGE_TRIP_B | (XT) String Low Voltage Trip Phase B | IPUDCDC | LOW | 200 | 0 |  |  |  | RESTART | FORCED | CFG_REDUNDANT
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 12 | 0x40 | X | 4 | 0x40X40C | ERROR_CODES::IPU::vDCDC::EXT1 | STRING_LOW_VOLTAGE_TRIP_C | (XT) String Low Voltage Trip Phase C | IPUDCDC | LOW | 200 | 0 |  |  |  | RESTART | FORCED | CFG_REDUNDANT
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 13 | 0x40 | X | 4 | 0x40X40D | ERROR_CODES::IPU::vDCDC::EXT1 | STRING_CURRENT_TRIP_1 | (XT) String Current RMS Trip Phase 1 | IPUDCDC | HIGH | 85 | 0 |  |  |  | RESTART | SHUTDOWN | CFG_REDUNDANT | not implemented
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 14 | 0x40 | X | 4 | 0x40X40E | ERROR_CODES::IPU::vDCDC::EXT1 | STRING_CURRENT_TRIP_2 | (XT) String Current RMS Trip Phase 2 | IPUDCDC | HIGH | 85 | 0 |  |  |  | RESTART | SHUTDOWN | CFG_REDUNDANT | not implemented
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 15 | 0x40 | X | 4 | 0x40X40F | ERROR_CODES::IPU::vDCDC::EXT1 | STRING_CURRENT_TRIP_3 | (XT) String Current RMS Trip Phase 3 | IPUDCDC | HIGH | 85 | 0 |  |  |  | RESTART | SHUTDOWN | CFG_REDUNDANT | not implemented
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 0 | 0x40 | X | 8 | 0x40X800 | ERROR_CODES::IPU::vDCDC::EXT2 | UDC_P_TRIP | (XT) DC-Link Positive Voltage Fault | IPUDCDC | HIGH | 900 | 0 |  |  |  | RESTART | FORCED | CFG_REDUNDANT
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 1 | 0x40 | X | 8 | 0x40X801 | ERROR_CODES::IPU::vDCDC::EXT2 | HARDWARE_TRIP | (XT) Hardware Trip | IPUDCDC | BOOL |  | 0 |  |  |  |  | SHUTDOWN | CFG_REDUNDANT | kein Acknowlege möglich laut Enasys
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 2 | 0x40 | X | 8 | 0x40X802 | ERROR_CODES::IPU::vDCDC::EXT2 | PRECHARGE_TRIP | (XT) Precharge Trip | IPUDCDC | BOOL |  | 0 |  |  |  | RESTART | SHUTDOWN | CFG_REDUNDANT
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 3 | 0x40 | X | 8 | 0x40X803 | ERROR_CODES::IPU::vDCDC::EXT2 | STATE_TRIP | (XT) State Trip | IPUDCDC | BOOL |  | 0 |  |  |  | RESTART | SHUTDOWN | CFG_REDUNDANT
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 4 | 0x40 | X | 8 | 0x40X804 | ERROR_CODES::IPU::vDCDC::EXT2 | ENABLE24_OFF | (XT) ENABLE 24V OFF | IPUDCDC | BOOL |  | 0 |  |  |  | RESTART | SHUTDOWN | CFG_REDUNDANT
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 5 | 0x40 | X | 8 | 0x40X805 | ERROR_CODES::IPU::vDCDC::EXT2 | LINKVOLT_NOT_VALID_FOR_CONNECTING_DCDC | (XT) Ulink is not valid for connecting DCDC | IPUDCDC | BOOL |  | 0 |  |  |  |  | SHUTDOWN | CFG_REDUNDANT
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 6 | 0x40 | X | 8 | 0x40X806 | ERROR_CODES::IPU::vDCDC::EXT2 | INDIVIDUAL_SM_TIMEOUT | (XT) IPU Statemachine timeout | IPUDCDC | BOOL |  | 0 |  |  |  |  | SHUTDOWN | CFG_REDUNDANT
Hardware | Enasys | IPU | Sharc | IPU3LInspector | 7 | 0x40 | X | 8 | 0x40X807 | ERROR_CODES::IPU::vDCDC::EXT2 | WRONGIPUTYPE | (XT) Incorrect IPU type detected | IPUDCDC | BOOL |  | 0 |  |  |  |  | SHUTDOWN | CFG_REDUNDANT
Hardware | AixControl | MIO30D | FPGA | ErrorIRQ | 0 | 0x30 | X | 1 | 0x30X100 | ERROR_CODES::IPU::VBE::COM | VOLTAGE_TRIP | AC Supply Trip | SHARC | Extern | [6 empty] | SHUTDOWN | SYSTEM
Hardware | AixControl | MIO30D | FPGA | ErrorIRQ | 9 | 0x30 | X | 1 | 0x30X109 | ERROR_CODES::IPU::VBE::COM | WATCHDOG_TRIP | Watchdog Timeout | SHARC | Extern | [6 empty] | FORCED | SYSTEM
Hardware | AixControl | MIO30D | FPGA | ErrorIRQ | 10 | 0x30 | X | 1 | 0x30X10A | ERROR_CODES::IPU::VBE::COM | CURRENT_LOOP_TRIP | CurrentLoop Open | SHARC | Extern | [6 empty] | FORCED | SYSTEM
Hardware | AixControl | MIO30D | FPGA | ErrorIRQ | 0 | 0x30 | X | 4 | 0x30X400 | ERROR_CODES::IPU::VBE::EXT1 | PLC_TRIP_FAST | (XT) PLC Trip Fast | SHARC | BOOL |  | 0 |  |  |  |  | WARNING | SYSTEM | Fault levels of VBE::EXT1 is WARNING because CCU TRIP dig. output should not be set. Reaction implemented in VBEFacade
Hardware | AixControl | MIO30D | FPGA | ErrorIRQ | 1 | 0x30 | X | 4 | 0x30X401 | ERROR_CODES::IPU::VBE::EXT1 | PLC_TRIP_SEQUENCED | (XT) PLC Trip Sequenced | SHARC | BOOL |  | 0 |  |  |  |  | WARNING | SYSTEM
Hardware | AixControl | MIO30D | FPGA | ErrorIRQ | 2 | 0x30 | X | 4 | 0x30X402 | ERROR_CODES::IPU::VBE::EXT1 | VBE_TRIP_FAST | (XT) VBE Trip Fast | SHARC | BOOL |  | 0 |  |  |  |  | WARNING | SYSTEM
Hardware | AixControl | MIO30D | FPGA | ErrorIRQ | 3 | 0x30 | X | 4 | 0x30X403 | ERROR_CODES::IPU::VBE::EXT1 | VBE_TRIP_SEQUENCED | (XT) VBE Trip Sequenced | SHARC | BOOL |  | 0 |  |  |  |  | WARNING | SYSTEM
Hardware | AixControl | MIO30D | FPGA | ErrorIRQ | 4 | 0x30 | X | 4 | 0x30X404 | ERROR_CODES::IPU::VBE::EXT1 | KZ04_TRIP_FAST | (XT) KZ04 Trip Fast | SHARC | BOOL |  | 0 |  |  |  |  | WARNING | SYSTEM
Hardware | AixControl | MIO | FPGA | ErrorIRQ | 0 | 0x10 | X | 1 | 0x10X100 | ERROR_CODES::MIO::v3V4C::AIXC | VOLTAGE_TRIP | AC Supply Trip | SHARC | Extern | [6 empty] | SHUTDOWN | SYSTEM
Hardware | AixControl | MIO | FPGA | ErrorIRQ | 9 | 0x10 | X | 1 | 0x10X109 | ERROR_CODES::MIO::v3V4C::AIXC | WATCHDOG_TRIP | Watchdog Timeout | SHARC | Extern | [6 empty] | SHUTDOWN | SYSTEM
Hardware | AixControl | MIO | FPGA | ErrorIRQ | 10 | 0x10 | X | 1 | 0x10X10A | ERROR_CODES::MIO::v3V4C::AIXC | CURRENT_LOOP_TRIP | CurrentLoop Open | SHARC | Extern | [6 empty] | SHUTDOWN | SYSTEM
Hardware | AixControl | MIO | Sharc | MIO3V4CInspector | 0 | 0x10 | X | 4 | 0x10X400 | ERROR_CODES::MIO::v3V4C::EXT1 | INTERN_TEMP_LOW | (XT) Warning: Internal Temperature Low | SHARC | LOW | 0 | 1 | 5 |  |  | AUTOACK | WARNING | SYSTEM
Hardware | AixControl | MIO | Sharc | MIO3V4CInspector | 1 | 0x10 | X | 4 | 0x10X401 | ERROR_CODES::MIO::v3V4C::EXT1 | INTERN_TEMP_HIGH | (XT) Warning: Internal Temperature High | SHARC | HIGH | 45 | 1 | 35 |  |  | AUTOACK | WARNING | SYSTEM
Grid | AixControl | MIO | Sharc | MIO3V4CInspector | 2 | 0x10 | X | 4 | 0x10X402 | ERROR_CODES::MIO::v3V4C::EXT1 | VOLT_1_LOW_WARNING | (XT) Warning: Voltage Low Phase 1 | SHARC | LOW | UNET*0.90 | 3 | UNET*0.91 |  |  | AUTOACK | WARNING | SYSTEM
Grid | AixControl | MIO | Sharc | MIO3V4CInspector | 3 | 0x10 | X | 4 | 0x10X403 | ERROR_CODES::MIO::v3V4C::EXT1 | VOLT_2_LOW_WARNING | (XT) Warning: Voltage Low Phase 2 | SHARC | LOW | UNET*0.90 | 3 | UNET*0.91 |  |  | AUTOACK | WARNING | SYSTEM
Grid | AixControl | MIO | Sharc | MIO3V4CInspector | 4 | 0x10 | X | 4 | 0x10X404 | ERROR_CODES::MIO::v3V4C::EXT1 | VOLT_3_LOW_WARNING | (XT) Warning: Voltage Low Phase 3 | SHARC | LOW | UNET*0.90 | 3 | UNET*0.91 |  |  | AUTOACK | WARNING | SYSTEM
Grid | AixControl | MIO | Sharc | MIO3V4CInspector | 5 | 0x10 | X | 4 | 0x10X405 | ERROR_CODES::MIO::v3V4C::EXT1 | VOLT_1_HIGH_WARNING | (XT) Warning: Voltage High Phase 1 | SHARC | HIGH | UNET*1.10 | 3 | UNET*1.09 |  |  | AUTOACK | WARNING | SYSTEM
Grid | AixControl | MIO | Sharc | MIO3V4CInspector | 6 | 0x10 | X | 4 | 0x10X406 | ERROR_CODES::MIO::v3V4C::EXT1 | VOLT_2_HIGH_WARNING | (XT) Warning: Voltage High Phase 2 | SHARC | HIGH | UNET*1.10 | 3 | UNET*1.09 |  |  | AUTOACK | WARNING | SYSTEM
Grid | AixControl | MIO | Sharc | MIO3V4CInspector | 7 | 0x10 | X | 4 | 0x10X407 | ERROR_CODES::MIO::v3V4C::EXT1 | VOLT_3_HIGH_WARNING | (XT) Warning: Voltage High Phase 3 | SHARC | HIGH | UNET*1.10 | 3 | UNET*1.09 |  |  | AUTOACK | WARNING | SYSTEM
Grid | AixControl | MIO | Sharc | MIO3V4CInspector | 8 | 0x10 | X | 4 | 0x10X408 | ERROR_CODES::MIO::v3V4C::EXT1 | VOLT_1_THD_WARNING | (XT) Warning: Voltage THD High Phase 1 | SHARC | HIGH | THD_WARN | 3 |  |  |  | AUTOACK | WARNING | SYSTEM
Grid | AixControl | MIO | Sharc | MIO3V4CInspector | 9 | 0x10 | X | 4 | 0x10X409 | ERROR_CODES::MIO::v3V4C::EXT1 | VOLT_2_THD_WARNING | (XT) Warning: Voltage THD High Phase 2 | SHARC | HIGH | THD_WARN | 3 |  |  |  | AUTOACK | WARNING | SYSTEM
Grid | AixControl | MIO | Sharc | MIO3V4CInspector | 10 | 0x10 | X | 4 | 0x10X40A | ERROR_CODES::MIO::v3V4C::EXT1 | VOLT_3_THD_WARNING | (XT) Warning: Voltage THD High Phase 3 | SHARC | HIGH | THD_WARN | 3 |  |  |  | AUTOACK | WARNING | SYSTEM
Grid | AixControl | MIO | Sharc | MIO3V4CInspector | 11 | 0x10 | X | 4 | 0x10X40B | ERROR_CODES::MIO::v3V4C::EXT1 | VOLT_1_LOW_TRIP | (XT) Voltage Low Trip Phase 1 | SHARC | LOW | UNET*0.85 | 0 |  |  |  | RESTART | SHUTDOWN | SYSTEM
Grid | AixControl | MIO | Sharc | MIO3V4CInspector | 12 | 0x10 | X | 4 | 0x10X40C | ERROR_CODES::MIO::v3V4C::EXT1 | VOLT_2_LOW_TRIP | (XT) Voltage Low Trip Phase 2 | SHARC | LOW | UNET*0.85 | 0 |  |  |  | RESTART | SHUTDOWN | SYSTEM
Grid | AixControl | MIO | Sharc | MIO3V4CInspector | 13 | 0x10 | X | 4 | 0x10X40D | ERROR_CODES::MIO::v3V4C::EXT1 | VOLT_3_LOW_TRIP | (XT) Voltage Low Trip Phase 3 | SHARC | LOW | UNET*0.85 | 0 |  |  |  | RESTART | SHUTDOWN | SYSTEM
Grid | AixControl | MIO | Sharc | MIO3V4CInspector | 14 | 0x10 | X | 4 | 0x10X40E | ERROR_CODES::MIO::v3V4C::EXT1 | VOLT_1_HIGH_TRIP | (XT) Voltage High Trip Phase 1 | SHARC | HIGH | UNET*1.15 | 0 |  |  |  | RESTART | SHUTDOWN | SYSTEM
Grid | AixControl | MIO | Sharc | MIO3V4CInspector | 15 | 0x10 | X | 4 | 0x10X40F | ERROR_CODES::MIO::v3V4C::EXT1 | VOLT_2_HIGH_TRIP | (XT) Voltage High Trip Phase 2 | SHARC | HIGH | UNET*1.15 | 0 |  |  |  | RESTART | SHUTDOWN | SYSTEM
Grid | AixControl | MIO | Sharc | MIO3V4CInspector | 16 | 0x10 | X | 4 | 0x10X410 | ERROR_CODES::MIO::v3V4C::EXT1 | VOLT_3_HIGH_TRIP | (XT) Voltage High Trip Phase 3 | SHARC | HIGH | UNET*1.15 | 0 |  |  |  | RESTART | SHUTDOWN | SYSTEM
Grid | AixControl | MIO | Sharc | MIO3V4CInspector | 17 | 0x10 | X | 4 | 0x10X411 | ERROR_CODES::MIO::v3V4C::EXT1 | VOLT_1_THD_TRIP | (XT) Voltage THD Trip Phase 1 | SHARC | HIGH | THD_LIM | 0 |  |  |  |  | FORCED | SYSTEM
Grid | AixControl | MIO | Sharc | MIO3V4CInspector | 18 | 0x10 | X | 4 | 0x10X412 | ERROR_CODES::MIO::v3V4C::EXT1 | VOLT_2_THD_TRIP | (XT) Voltage THD Trip Phase 2 | SHARC | HIGH | THD_LIM | 0 |  |  |  |  | FORCED | SYSTEM
Grid | AixControl | MIO | Sharc | MIO3V4CInspector | 19 | 0x10 | X | 4 | 0x10X413 | ERROR_CODES::MIO::v3V4C::EXT1 | VOLT_3_THD_TRIP | (XT) Voltage THD Trip Phase 3 | SHARC | HIGH | THD_LIM | 0 |  |  |  |  | FORCED | SYSTEM
Grid | AixControl | MIO | Sharc | MIO3V4CInspector | 20 | 0x10 | X | 4 | 0x10X414 | ERROR_CODES::MIO::v3V4C::EXT1 | FREQUENCY_LOW_TRIP | (XT) Frequency Low Trip | SHARC | LOW | FREQ-5.f | 5 |  |  |  |  | SHUTDOWN | SYSTEM
Grid | AixControl | MIO | Sharc | MIO3V4CInspector | 21 | 0x10 | X | 4 | 0x10X415 | ERROR_CODES::MIO::v3V4C::EXT1 | FREQUENCY_HIGH_TRIP | (XT) Frequency High Trip | SHARC | HIGH | FREQ+5.f | 5 |  |  |  |  | SHUTDOWN | SYSTEM
Grid | AixControl | MIO | Sharc | MIO3V4CInspector | 22 | 0x10 | X | 4 | 0x10X416 | ERROR_CODES::MIO::v3V4C::EXT1 | PHASE_ORDER_TRIP | (XT) Invalid Phase Order Trip | SHARC | BOOL |  | 0 |  |  |  | RESTART | SHUTDOWN | SYSTEM
Grid | AixControl | MIO | Sharc | MIO3V4CInspector | 23 | 0x10 | X | 4 | 0x10X417 | ERROR_CODES::MIO::v3V4C::EXT1 | VOLT_1_SRD_WARNING | (XT) Selective Resonance Detection (SRD) Phase 1 | SHARC | BOOL |  | 0 |  |  |  | AUTOACK | WARNING | SYSTEM | not implemented
Grid | AixControl | MIO | Sharc | MIO3V4CInspector | 24 | 0x10 | X | 4 | 0x10X418 | ERROR_CODES::MIO::v3V4C::EXT1 | VOLT_2_SRD_WARNING | (XT) Selective Resonance Detection (SRD) Phase 2 | SHARC | BOOL |  | 0 |  |  |  | AUTOACK | WARNING | SYSTEM | not implemented
Grid | AixControl | MIO | Sharc | MIO3V4CInspector | 25 | 0x10 | X | 4 | 0x10X419 | ERROR_CODES::MIO::v3V4C::EXT1 | VOLT_3_SRD_WARNING | (XT) Selective Resonance Detection (SRD) Phase 3 | SHARC | BOOL |  | 0 |  |  |  | AUTOACK | WARNING | SYSTEM | not implemented
Grid | AixControl | MIO | Sharc | MIO3V4CInspector | 26 | 0x10 | X | 4 | 0x10X41A | ERROR_CODES::MIO::v3V4C::EXT1 | FREQUENCY_DFDT_TRIP | (XT) Frequency Change Rate Trip | SHARC | HIGH | 4 | 0 |  |  |  |  | SHUTDOWN | SYSTEM | PQAA-5225 - Frequency Change-rate Lakeland
DSC | AixControl | DSC | Sharc | COMInspector | 0 | 0x06 | 0 | 0 | 0x060000 | ERROR_CODES::COM | MERKUR_PORT0 | DSC 10 removed !Restart! | SHARC | BOOL |  | 0 |  |  |  | NOACK | SHUTDOWN | SYSTEM
DSC | AixControl | DSC | Sharc | COMInspector | 1 | 0x06 | 0 | 0 | 0x060001 | ERROR_CODES::COM | MERKUR_PORT1 | DSC 9 removed !Restart! | SHARC | BOOL |  | 0 |  |  |  | NOACK | SHUTDOWN | SYSTEM
DSC | AixControl | DSC | Sharc | COMInspector | 2 | 0x06 | 0 | 0 | 0x060002 | ERROR_CODES::COM | MERKUR_PORT2 | DSC 8 removed !Restart! | SHARC | BOOL |  | 0 |  |  |  | NOACK | SHUTDOWN | SYSTEM
DSC | AixControl | DSC | Sharc | COMInspector | 3 | 0x06 | 0 | 0 | 0x060003 | ERROR_CODES::COM | MERKUR_PORT3 | DSC 7 removed !Restart! | SHARC | BOOL |  | 0 |  |  |  | NOACK | SHUTDOWN | SYSTEM
DSC | AixControl | DSC | Sharc | COMInspector | 4 | 0x06 | 0 | 0 | 0x060004 | ERROR_CODES::COM | MERKUR_PORT4 | DSC 6 removed !Restart! | SHARC | BOOL |  | 0 |  |  |  | NOACK | SHUTDOWN | SYSTEM
DSC | AixControl | DSC | Sharc | COMInspector | 5 | 0x06 | 0 | 0 | 0x060005 | ERROR_CODES::COM | MERKUR_PORT5 | DSC 5 removed !Restart! | SHARC | BOOL |  | 0 |  |  |  | NOACK | SHUTDOWN | SYSTEM
DSC | AixControl | DSC | Sharc | COMInspector | 6 | 0x06 | 0 | 0 | 0x060006 | ERROR_CODES::COM | MERKUR_PORT6 | DSC 4 removed !Restart! | SHARC | BOOL |  | 0 |  |  |  | NOACK | SHUTDOWN | SYSTEM
DSC | AixControl | DSC | Sharc | COMInspector | 7 | 0x06 | 0 | 0 | 0x060007 | ERROR_CODES::COM | MERKUR_PORT7 | DSC 3 removed !Restart! | SHARC | BOOL |  | 0 |  |  |  | NOACK | SHUTDOWN | SYSTEM
DSC | AixControl | DSC | Sharc | COMInspector | 8 | 0x06 | 0 | 0 | 0x060008 | ERROR_CODES::COM | MERKUR_PORT8 | DSC 2 removed !Restart! | SHARC | BOOL |  | 0 |  |  |  | NOACK | SHUTDOWN | SYSTEM
DSC | AixControl | DSC | Sharc | COMInspector | 9 | 0x06 | 0 | 0 | 0x060009 | ERROR_CODES::COM | MERKUR_PORT9 | DSC 1 removed !Restart! | SHARC | BOOL |  | 0 |  |  |  | NOACK | SHUTDOWN | SYSTEM
Software | AixControl | Blackfin | Sharc | COMInspector | 10 | 0x06 | 0 | 0 | 0x06000A | ERROR_CODES::COM | INPUT_SLOT | InputSlot Timeout | SHARC | BOOL |  | 15 |  |  |  |  | SHUTDOWN | SYSTEM
Software | AixControl | Sharc | Blackfin | ReceiveTask | 11 | 0x06 | 0 | 0 | 0x06000B | ERROR_CODES::COM | COM_SLOT | CommunicationSlot Timeout | Blackfin | BOOL |  | 10 |  |  |  |  | SHUTDOWN | SYSTEM
Software | AixControl | Sharc | Blackfin | ReceiveTask | 12 | 0x06 | 0 | 0 | 0x06000C | ERROR_CODES::COM | STATUS_SLOT | StatusSlot Timeout | Blackfin | BOOL |  | 20 |  |  |  |  | WARNING | SYSTEM
Software | AixControl | Sharc | Sharc | COMInspector | 13 | 0x06 | 0 | 0 | 0x06000D | ERROR_CODES::COM | WHILE_LOOP | While Loop Timeout | SHARC | BOOL |  | 3 |  |  |  |  | SHUTDOWN | SYSTEM
DSC | AixControl | DSC | Sharc | COMInspector | 14 | 0x06 | 0 | 0 | 0x06000E | ERROR_CODES::COM | IRQ_TIMEOUT | Interrupt Request Timeout | SHARC | BOOL |  | 0 |  |  |  |  | SHUTDOWN | SYSTEM
Software | AixControl | SPORT | Sharc | COMInspector | 15 | 0x06 | 0 | 0 | 0x06000F | ERROR_CODES::COM | SH_BUFFER | Sharc Buffer Overflow | SHARC | HIGH | 94 | 0 |  |  |  |  | SHUTDOWN | SYSTEM
Software | AixControl | SPORT | Blackfin | COMInspector | 15 | 0x06 | 0 | 0 | 0x06000F | ERROR_CODES::COM | SH_BUFFER | Sharc Buffer Overflow | Blackfin | HIGH | 94 | 0 |  |  |  |  | WARNING | SYSTEM
Software | AixControl | SPORT | Blackfin | COMInspector | 16 | 0x06 | 0 | 0 | 0x060010 | ERROR_CODES::COM | BF_BUFFER | Blackfin Buffer Overflow | Blackfin | HIGH | 150 | 0 | 100 | 5 |  | AUTOACK | WARNING | SYSTEM
DSC | AixControl | CCU Master | Sharc | COMInspector | 17 | 0x06 | 0 | 0 | 0x060011 | ERROR_CODES::COM | S_INACTIVE | Master Inactive @ Slave | SHARC | BOOL |  | 0 |  |  |  |  | FORCED | SYSTEM | Communication to master is inactive
DSC | AixControl | CCU Master | Sharc | COMInspector | 18 | 0x06 | 0 | 0 | 0x060012 | ERROR_CODES::COM | S_INVALID | Master Packet Invalid @ Slave | SHARC | BOOL |  | 0 |  |  |  |  | FORCED | SYSTEM | Too much invalid data from master
Software | MR | StateMachine | Sharc | COMInspector | 19 | 0x06 | 0 | 0 | 0x060013 | ERROR_CODES::COM | AUTOSTART_ENABLED | Autostart enabled | SHARC | BOOL |  | 0 |  |  |  | AUTOACK | WARNING | SYSTEM
Hardware |  | Fan | Sharc | COMInspector | 20 | 0x06 | 0 | 0 | 0x060014 | ERROR_CODES::COM | LCU_PRESSURE_LOSS | LCU pressure loss trip | SHARC | BOOL |  | 0 |  |  |  | RESTART | SHUTDOWN | SYSTEM
Hardware |  | Fan | Sharc | COMInspector | 21 | 0x06 | 0 | 0 | 0x060015 | ERROR_CODES::COM | LCU_TEMPERTURE_HIGH | LCU temperature high | SHARC | BOOL |  | 0 |  |  |  | AUTOACK | WARNING | SYSTEM
Hardware | AixControl | MIO | Sharc | COMInspector | 22 | 0x06 | 0 | 0 | 0x060016 | ERROR_CODES::COM | DIGITAL_SYSTEMLOCK | Digital Input : System Locked | SHARC | BOOL |  | 0 |  | 15 |  | AUTOACK | WARNING | SYSTEM
Peripherials | EPCOS | Pro-CX | Modbus | 80 | 0 | 0x06 | 0 | 0 | 0x060017 | ERROR_CODES::COM | PROCX_EXTERN | Pro-CX: External error | Blackfin | Extern | [6 empty] | WARNING | SINGLE
Peripherials | EPCOS | Pro-CX | Modbus | 80 | 1 | 0x06 | 0 | 0 | 0x060018 | ERROR_CODES::COM | PROCX_OVERVOLTAGE | Pro-CX: Overvoltage | Blackfin | Extern | [6 empty] | WARNING | SINGLE
Peripherials | EPCOS | Pro-CX | Modbus | 80 | 2 | 0x06 | 0 | 0 | 0x060019 | ERROR_CODES::COM | PROCX_OVERCOMPENSATED | Pro-CX: Overcompensated | Blackfin | Extern | [6 empty] | WARNING | SINGLE
Peripherials | EPCOS | Pro-CX | Modbus | 80 | 3 | 0x06 | 0 | 0 | 0x06001A | ERROR_CODES::COM | PROCX_UNDERCOMPENSATED | Pro-CX: Undercompensated | Blackfin | Extern | [6 empty] | WARNING | SINGLE
Peripherials | EPCOS | Pro-CX | Modbus | 80 | 4 | 0x06 | 0 | 0 | 0x06001B | ERROR_CODES::COM | PROCX_HARMONICS | Pro-CX: Harmonics | Blackfin | Extern | [6 empty] | WARNING | SINGLE
Peripherials | EPCOS | Pro-CX | Modbus | 80 | 5 | 0x06 | 0 | 0 | 0x06001C | ERROR_CODES::COM | PROCX_TEMPERATURE | Pro-CX: Temperature high | Blackfin | Extern | [6 empty] | WARNING | SINGLE
Peripherials | EPCOS | Pro-CX | Modbus | 80 | 6 | 0x06 | 0 | 0 | 0x06001D | ERROR_CODES::COM | PROCX_UNDERCURRENT | Pro-CX: Undercurrent | Blackfin | Extern | [6 empty] | WARNING | SINGLE
Peripherials | EPCOS | Pro-CX | Modbus | 80 | 7 | 0x06 | 0 | 0 | 0x06001E | ERROR_CODES::COM | PROCX_UNDERVOLTAGE | Pro-CX: Undervoltage | Blackfin | Extern | [6 empty] | WARNING | SINGLE
Peripherials | EPCOS | Pro-CX | Blackfin | CPFCProCX | 31 | 0x06 | 0 | 0 | 0x06001F | ERROR_CODES::COM | PROCX_COMMUNICATION | Pro-CX Communication Error | Blackfin | BOOL |  | 10 |  |  |  |  | WARNING | SINGLE
Software | MR | Control | Sharc | COMInspector | 0 | 0x06 | 0 | 0 | 0x060020 | ERROR_CODES::COM2 | DERATING_RMS_CURRENT | Derating: RMS current | SHARC | BOOL |  | 1 |  | 15 |  | AUTOACK | CFG_DERATING | SYSTEM
Software | MR | Control | Sharc | COMInspector | 1 | 0x06 | 0 | 0 | 0x060021 | ERROR_CODES::COM2 | DERATING_PEAK_GRIDCURRENT | Derating: Output peak current | SHARC | BOOL |  | 1 |  | 15 |  | AUTOACK | CFG_DERATING | SYSTEM
Software | MR | Control | Sharc | COMInspector | 2 | 0x06 | 0 | 0 | 0x060022 | ERROR_CODES::COM2 | DERATING_PEAK_MODULECURRENT | Derating: IGBT peak current | SHARC | BOOL |  | 1 |  | 15 |  | AUTOACK | CFG_DERATING | SYSTEM
Software | MR | Control | Sharc | COMInspector | 3 | 0x06 | 0 | 0 | 0x060023 | ERROR_CODES::COM2 | DERATING_MODULATIONSINDEX | Derating: Modulation limit | SHARC | BOOL |  | 1 |  | 15 |  | AUTOACK | CFG_DERATING | SYSTEM
Software | MR | Control | Sharc | COMInspector | 4 | 0x06 | 0 | 0 | 0x060024 | ERROR_CODES::COM2 | DERATING_DC_VOLTAGE_UNBALANCE | Derating: DC voltage unbalance | SHARC | BOOL |  | 1 |  | 15 |  | AUTOACK | CFG_DERATING | SYSTEM
Software | MR | Control | Sharc | COMInspector | 5 | 0x06 | 0 | 0 | 0x060025 | ERROR_CODES::COM2 | DERATING_DC_VOLTAGE_MAXIMUM | Derating: DC voltage limit | SHARC | BOOL |  | 1 |  | 15 |  | AUTOACK | CFG_DERATING | SYSTEM
Software | MR | Control | Sharc | COMInspector | 6 | 0x06 | 0 | 0 | 0x060026 | ERROR_CODES::COM2 | DERATING_CHOKE_TEMPERATURE | Derating: Choke temperature | SHARC | BOOL |  | 1 |  | 15 |  | AUTOACK | CFG_DERATING | SYSTEM
Software | MR | Control | Sharc | COMInspector | 7 | 0x06 | 0 | 0 | 0x060027 | ERROR_CODES::COM2 | DERATING_IGBT_TEMPERATURE | Derating: IGBT temperature | SHARC | BOOL |  | 1 |  | 15 |  | AUTOACK | CFG_DERATING | SYSTEM
Software | MR | Control | Sharc | COMInspector | 8 | 0x06 | 0 | 0 | 0x060028 | ERROR_CODES::COM2 | DERATING_MCU_TEMPERATURE | Derating: MCU temperature | SHARC | BOOL |  | 1 |  | 15 |  | AUTOACK | CFG_DERATING | SYSTEM
Software | MR | Control | Sharc | COMInspector | 9 | 0x06 | 0 | 0 | 0x060029 | ERROR_CODES::COM2 | DERATING_GRID_VOLTAGE | Derating: GridVoltage | SHARC | BOOL |  | 1 |  | 15 |  | AUTOACK | CFG_DERATING | SYSTEM
Software | MR | Control | Sharc | COMInspector | 10 | 0x06 | 0 | 0 | 0x06002A | ERROR_CODES::COM2 | DERATING_NEUTRAL_CURRENT | Derating: RMS current neutral | SHARC | BOOL |  | 1 |  | 15 |  | AUTOACK | CFG_DERATING | SYSTEM
Software | MR | StateMachine | Sharc | COMInspector | 11 | 0x06 | 0 | 0 | 0x06002B | ERROR_CODES::COM2 | STARTSTOP_MODE | Auto start-stop active | SHARC | BOOL |  | 0 |  |  |  | AUTOACK | WARNING | SYSTEM
Software | MR | CCU | Sharc | COMInspector | 12 | 0x06 | 0 | 0 | 0x06002C | ERROR_CODES::COM2 | WARMSTART | CCU warm restart triggered | [8 empty] | INFO
Software | MR | Control | Sharc | COMInspector | 13 | 0x06 | 0 | 0 | 0x06002D | ERROR_CODES::COM2 | SIA_RUNNING | (XT) System Identification Algorithm (SIA) running... | SHARC | BOOL |  | 0 |  |  |  | AUTOACK | WARNING | SYSTEM
Software | MR | Control | Sharc | COMInspector | 14 | 0x06 | 0 | 0 | 0x06002E | ERROR_CODES::COM2 | SIA_WARNING | (XT) SIA Warning | SHARC | BOOL |  | 0 |  |  |  | AUTOACK | WARNING | SYSTEM
Software | MR | Control | Sharc | COMInspector | 15 | 0x06 | 0 | 0 | 0x06002F | ERROR_CODES::COM2 | SUSPECT_HARMONICS_DETECTED | (XT) Suspect Harmonics marked | SHARC | BOOL |  | 0 |  |  |  | AUTOACK | WARNING | SYSTEM
Software | MR | Control | Sharc | COMInspector | 16 | 0x06 | 0 | 0 | 0x060030 | ERROR_CODES::COM2 | CRITICAL_HARMONICS_DETECTED | (XT) Compensation of critical harmonics blocked | SHARC | BOOL |  | 0 |  |  |  | AUTOACK | WARNING | SYSTEM
Software | MR | Control | Sharc | COMInspector | 17 | 0x06 | 0 | 0 | 0x060031 | ERROR_CODES::COM2 | VOLTAGE_NOT_VALID_FOR_START_ACDCs | (XT) VOLT NOT VALID START ACDC | SHARC | BOOL |  | 0 |  |  |  |  | SHUTDOWN | CFG_REDUNDANT
Software | MR | Control | Sharc | COMInspector | 18 | 0x06 | 0 | 0 | 0x060032 | ERROR_CODES::COM2 | FREQUENZ_NOT_VALID_FOR_START_ACDCs | (XT) FREQ NOT VALID START ACDC | SHARC | BOOL |  | 0 |  |  |  |  | SHUTDOWN | CFG_REDUNDANT
Software | MR | Software | Sharc / Blackfin | ErrorParameters | 0 | 0x01 | 0 | 0 | 0x010000 | ERROR_CODES::SW | PARAM_UNDEFINED | Undefined fault parameter | Common | Extern | [6 empty] | SHUTDOWN | SYSTEM | Acknowledge not possible
Software | MR | Software | Sharc / Blackfin | ErrorParameters | 1 | 0x01 | 0 | 0 | 0x010001 | ERROR_CODES::SW | PARAM_NULL_POINTER | Null pointer to fault parameter | Common | Extern | [6 empty] | SHUTDOWN | SYSTEM | Acknowledge not possible
Software | MR | Software | Sharc / Blackfin | ErrorParameters | 2 | 0x01 | 0 | 0 | 0x010002 | ERROR_CODES::SW | INVALID_PARAMETER | Invalid fault parameter | Common | Extern | [6 empty] | SHUTDOWN | SYSTEM | Acknowledge not possible
Software | MR | Software | Sharc / Blackfin | Cinspector | 3 | 0x01 | 0 | 0 | 0x010003 | ERROR_CODES::SW | GROUP_INSPECTOR_NULL | Undefined group inspector | Common | Extern | [6 empty] | SHUTDOWN | SYSTEM | Acknowledge not possible
Software | MR | Software | Sharc | MerkurInspector | 4 | 0x01 | 0 | 0 | 0x010004 | ERROR_CODES::SW | INVALID_CLIENT_ID | Invalid Merkur client ID | SHARC | Extern | [6 empty] | SHUTDOWN | SYSTEM
Software | MR | Software | Sharc / Blackfin | ErrorParameters | 5 | 0x01 | 0 | 0 | 0x010005 | ERROR_CODES::SW | INVALID_HIERARCHY | Invalid fault hierarchy | Common | Extern | [6 empty] | SHUTDOWN | SYSTEM | Acknowledge not possible
Software | MR | DSC | Blackfin | MerkurFacade | 6 | 0x01 | 0 | 0 | 0x010006 | ERROR_CODES::SW | MERKUR_INIT_FAIL | Merkur module initialization failed | SHARC | Extern | [6 empty] | WARNING | SYSTEM
Software | MR | DSC | Blackfin | MerkurFacade | 7 | 0x01 | 0 | 0 | 0x010007 | ERROR_CODES::SW | INVALID_MIO_ORDER | Invalid MIO ports sequence | SHARC | Extern | [6 empty] | SHUTDOWN | SYSTEM
Software | MR | Software | Sharc | Measurements | 8 | 0x01 | 0 | 0 | 0x010008 | ERROR_CODES::SW | PQM_INVALID_CONFIG | Invalid measurement configuration | SHARC | Extern | [6 empty] | SHUTDOWN | SYSTEM
Software | MR | Software | Sharc | Measurements | 9 | 0x01 | 0 | 0 | 0x010009 | ERROR_CODES::SW | PQM_CHANNELS_OVERFLOW | Measurement channels limit reached | SHARC | Extern | [6 empty] | SHUTDOWN | SYSTEM
Software | MR | Configuration | Blackfin | ConfigHMI | 10 | 0x01 | 0 | 0 | 0x01000A | ERROR_CODES::SW | PQM_INVALID_FORMAT | Invalid current sum configuration format | Blackfin | Extern | [6 empty] | SHUTDOWN | SYSTEM
Software | MR | Software | Sharc | Measurements | 11 | 0x01 | 0 | 0 | 0x01000B | ERROR_CODES::SW | PQM_CALCULATIONS_TIMEOUT | Measurements calculation timeout | SHARC | BOOL |  | 0 |  |  |  |  | WARNING | SYSTEM
Software | MR |  |  |  | 12 | 0x01 | 0 | 0 | 0x01000C | ERROR_CODES::SW | PQM_PACKET_MISSING | Measurement packet missing | Blackfin | Extern | [6 empty] | WARNING | SYSTEM | not implemented
Software | MR |  |  |  | 13 | 0x01 | 0 | 0 | 0x01000D | ERROR_CODES::SW | PQM_INVALID_DATA | Invalid measurement data | Blackfin | Extern | [6 empty] | WARNING | SYSTEM | not implemented
Software | MR | Software | Sharc | Userinterface | 14 | 0x01 | 0 | 0 | 0x01000E | ERROR_CODES::SW | RTDS_SOFTWARE | Warning: RTDS Version - Do not use on real hardware | SHARC | Extern | [6 empty] | INFO | SYSTEM
Software | MR | Software | Sharc / Blackfin |  | 15 | 0x01 | 0 | 0 | 0x01000F | ERROR_CODES::SW | ARRAY_OVERFLOW | Array oveflow | Common | Extern | [6 empty] | SHUTDOWN | SYSTEM | Acknowledge not possible
Software | MR | Software | Sharc |  | 16 | 0x01 | 0 | 0 | 0x010010 | ERROR_CODES::SW | AUTONOM_TEST_SW | Warning: AUTONOM TEST SW ( Autostart ) | SHARC | Extern | [6 empty] | INFO | SYSTEM
Software | MR | Software | Sharc | AutarsysFacade | 17 | 0x01 | 0 | 0 | 0x010011 | ERROR_CODES::SW | NO_BLACKSTART_OR_SYNC_ENABLED | no Blackstart or SyncV enabled | SHARC | Extern | [6 empty] | SHUTDOWN | SYSTEM
Software | MR | Software | Sharc | AutarsysFacade | 18 | 0x01 | 0 | 0 | 0x010012 | ERROR_CODES::SW | SYNC_V_AND_BLACKSTART_ENABLED | sycnV and Blackstart enabled | SHARC | Extern | [6 empty] | SHUTDOWN | SYSTEM
Software | MR | Software | Sharc | AutarsysFacade | 19 | 0x01 | 0 | 0 | 0x010013 | ERROR_CODES::SW | VOLTAGE_NOT_ZERO_FOR_BLACKSTART | voltage not zero for Blackstart | SHARC | Extern | [6 empty] | SHUTDOWN | SYSTEM
Software | MR | Software | Sharc | AutarsysFacade | 20 | 0x01 | 0 | 0 | 0x010014 | ERROR_CODES::SW | VOLTAGE_SYNC_NOT_SUCCEDDED | voltage sync not succedded | SHARC | Extern | [6 empty] | SHUTDOWN | SYSTEM
Software | MR | Software | Sharc | AutarsysFacade | 21 | 0x01 | 0 | 0 | 0x010015 | ERROR_CODES::SW | VOLTAGE_NOT_OK_FOR_SYNC_V | voltage not ok for sync V | SHARC | Extern | [6 empty] | SHUTDOWN | SYSTEM
Software | MR | Software | Sharc | AutarsysFacade | 22 | 0x01 | 0 | 0 | 0x010016 | ERROR_CODES::SW | GENERATOR_CONNECTED_WRONG_PHASE | generator connected wrong phase | SHARC | Extern | [6 empty] | SHUTDOWN | SYSTEM
Software | MR | Software | Sharc | AutarsysFacade | 23 | 0x01 | 0 | 0 | 0x010017 | ERROR_CODES::SW | FRT_FAULT | FRT Error occured | SHARC | Extern | [6 empty] | SHUTDOWN | SYSTEM
Software | MR | Software | Sharc | AutarsysFacade | 24 | 0x01 | 0 | 0 | 0x010018 | ERROR_CODES::SW | IDC_OVERCURRENT | DC-Link Overcurrent | Blackfin | HIGH | 140 | 0 |  |  |  |  | SHUTDOWN | SYSTEM
Software | MR | Software | Sharc / Blackfin | Measurements | 0 | 0x03 | 0 | 0 | 0x030000 | ERROR_CODES::PQM::CFG | SUMMANDS_OVERFLOW | Summands overflow | SHARC | Extern | [6 empty] | SHUTDOWN | SYSTEM
Software | MR | Software | Sharc / Blackfin | Measurements | 1 | 0x03 | 0 | 0 | 0x030001 | ERROR_CODES::PQM::CFG | CYCLIC_CONFIG | Cyclic current sum configuration | SHARC | Extern | [6 empty] | SHUTDOWN | SYSTEM
Software | MR | Software | Sharc / Blackfin | Measurements | 2 | 0x03 | 0 | 0 | 0x030002 | ERROR_CODES::PQM::CFG | INVALID_PHASE | Summand set to nonexistent phase | SHARC | Extern | [6 empty] | SHUTDOWN | SYSTEM
Software | MR | Software | Sharc / Blackfin | Measurements | 3 | 0x03 | 0 | 0 | 0x030003 | ERROR_CODES::PQM::CFG | INVALID_MIO_VOLTAGE | Nonexistent MIO voltage channel | SHARC | Extern | [6 empty] | SHUTDOWN | SYSTEM
Software | MR | Software | Sharc / Blackfin | Measurements | 4 | 0x03 | 0 | 0 | 0x030004 | ERROR_CODES::PQM::CFG | INVALID_MIO_CURRENT | Nonexistent MIO current channel | SHARC | Extern | [6 empty] | SHUTDOWN | SYSTEM
Software | MR | Software | Sharc / Blackfin | Measurements | 5 | 0x03 | 0 | 0 | 0x030005 | ERROR_CODES::PQM::CFG | INVALID_MIO_CURRENT_GROUPS | Inconsistent MIO current channels grouping | SHARC | Extern | [6 empty] | SHUTDOWN | SYSTEM
Software | MR | Software | Sharc / Blackfin | Measurements | 6 | 0x03 | 0 | 0 | 0x030006 | ERROR_CODES::PQM::CFG | INVALID_DEVICE_CHANNEL | Nonexistent device phase current | SHARC | Extern | [6 empty] | SHUTDOWN | SYSTEM
Software | MR | Software | Sharc / Blackfin | Measurements | 7 | 0x03 | 0 | 0 | 0x030007 | ERROR_CODES::PQM::CFG | CHANNEL_NULL | Measurement channel not initialized | SHARC | Extern | [6 empty] | SHUTDOWN | SYSTEM
Software | MR | Software | Sharc / Blackfin | Measurements | 8 | 0x03 | 0 | 0 | 0x030008 | ERROR_CODES::PQM::CFG | PHASE_MISSING | Device current configuration missing | SHARC | Extern | [6 empty] | SHUTDOWN | SYSTEM
Software | MR | Software | Sharc / Blackfin | Measurements | 9 | 0x03 | 0 | 0 | 0x030009 | ERROR_CODES::PQM::CFG | DEVICE_DISABLED | Initializing disabled device current | SHARC | Extern | [6 empty] | SHUTDOWN | SYSTEM
Peripherials | HMS | Anybus | Blackfin | ABCC_DriverHandler | 0 | 0x07 | 0 | 0 | 0x070000 | ERROR_CODES::ANY_ERR | ABCC_ERR_INVALID_PROC_WRITE_DATA_SIZE | Invalid write process data size | Blackfin | Extern | [6 empty] | CFG_ANYBUS | SYSTEM
Peripherials | HMS | Anybus | Blackfin | ABCC_DriverHandler | 1 | 0x07 | 0 | 0 | 0x070001 | ERROR_CODES::ANY_ERR | ABCC_ERR_INVALID_PROC_READ_DATA_SIZE | Invalid read process data size | Blackfin | Extern | [6 empty] | CFG_ANYBUS | SYSTEM
Peripherials | HMS | Anybus | Blackfin | ABCC_DriverHandler | 2 | 0x07 | 0 | 0 | 0x070002 | ERROR_CODES::ANY_ERR | ABCC_ERR_MODULE_MISSING | Module missing | Blackfin | Extern | [6 empty] | CFG_ANYBUS | SYSTEM
Peripherials | HMS | Anybus | Blackfin | ABCC_DriverHandler | 3 | 0x07 | 0 | 0 | 0x070003 | ERROR_CODES::ANY_ERR | ABCC_ERR_NODEID_NOT_SETABLE | Cannot set node ID | Blackfin | Extern | [6 empty] | CFG_ANYBUS | SYSTEM
Peripherials | HMS | Anybus | Blackfin | ABCC_DriverHandler | 4 | 0x07 | 0 | 0 | 0x070004 | ERROR_CODES::ANY_ERR | ABCC_ERR_ATTR_WRITE_ERROR | Cannot set attribute | Blackfin | Extern | [6 empty] | CFG_ANYBUS | SYSTEM
Peripherials | HMS | Anybus | Blackfin | ABCC_DriverHandler | 5 | 0x07 | 0 | 0 | 0x070005 | ERROR_CODES::ANY_ERR | ABCC_ERR_INIT_ATTR_READ_ERROR | Error reading attributes during initialization | Blackfin | Extern | [6 empty] | CFG_ANYBUS | SYSTEM
Peripherials | HMS | Anybus | Blackfin | ABCC_DriverHandler | 6 | 0x07 | 0 | 0 | 0x070006 | ERROR_CODES::ANY_ERR | ABCC_ERR_MODULE_WATCHDOG_TIMEOUT | Module watchdog timeout | Blackfin | Extern | [6 empty] | CFG_ANYBUS | SYSTEM
Peripherials | HMS | Anybus | Blackfin | ABCC_DriverHandler | 7 | 0x07 | 0 | 0 | 0x070007 | ERROR_CODES::ANY_ERR | ABCC_ERR_READING_EXCEPTION_CODE | Error reading exception code | Blackfin | Extern | [6 empty] | CFG_ANYBUS | SYSTEM
Peripherials | HMS | Anybus | Blackfin | ABCC_DriverHandler | 8 | 0x07 | 0 | 0 | 0x070008 | ERROR_CODES::ANY_ERR | ABCC_ERR_READING_NW_SPEC_EXCEPTION_CODE | Error reading network specific exception code | Blackfin | Extern | [6 empty] | CFG_ANYBUS | SYSTEM
Peripherials | HMS | Anybus | Blackfin | ABCC_DriverHandler | 9 | 0x07 | 0 | 0 | 0x070009 | ERROR_CODES::ANY_ERR | ABCC_ERR_NON_RECOVERABLE_EXCEPTION | Non-recoverable exception | Blackfin | Extern | [6 empty] | CFG_ANYBUS | SYSTEM
Peripherials | HMS | Anybus | Blackfin | ABCC_DriverHandler | 10 | 0x07 | 0 | 0 | 0x07000A | ERROR_CODES::ANY_ERR | ABCC_ERR_CONNECTION_TERMINATED | Connection terminated | Blackfin | BOOL |  | 0 |  |  |  |  | CFG_ANYBUS | SYSTEM
Peripherials | HMS | Anybus | Blackfin | ABCC_DriverHandler | 11 | 0x07 | 0 | 0 | 0x07000B | ERROR_CODES::ANY_ERR | ABCC_ERR_NETWORK_ERROR | Network error | Blackfin | Extern | [6 empty] | CFG_ANYBUS | SYSTEM
Peripherials | HMS | Anybus | Blackfin | ABCC_DriverHandler | 12 | 0x07 | 0 | 0 | 0x07000C | ERROR_CODES::ANY_ERR | ABCC_ERR_DRIVER_STATE_CHANGE_DENIED | Driver handler state change denied | Blackfin | Extern | [6 empty] | CFG_ANYBUS | SYSTEM
Peripherials | HMS | Anybus | Blackfin | ABCC_DriverHandler | 13 | 0x07 | 0 | 0 | 0x07000D | ERROR_CODES::ANY_ERR | ABCC_ERR_MAX_RESTART_COUNT | Module restart count limit reached | Blackfin | Extern | [6 empty] | CFG_ANYBUS | SYSTEM
Peripherials | HMS | Anybus | Blackfin | ABCC_DriverHandler | 14 | 0x07 | 0 | 0 | 0x07000E | ERROR_CODES::ANY_ERR | ABCC_ERR_MODULE_RESTART | Module restarted | Blackfin | Extern | [6 empty] | WARNING | SYSTEM
Peripherials | HMS | Anybus | Blackfin | ABCC_DriverHandler | 15 | 0x07 | 0 | 0 | 0x07000F | ERROR_CODES::ANY_ERR | ABCC_ERR_DRIVER_TERMINATED | Driver terminated | Blackfin | Extern | [6 empty] | CFG_ANYBUS | SYSTEM
Peripherials | HMS | Anybus | Blackfin | ABCC_DriverHandler | 0 | 0x07 | 0 | 0 | 0x070010 | ERROR_CODES::ANY_EXCPT | ABCC_EXCPT_APP_TO | Application timeout | Blackfin | Extern | [6 empty] | CFG_ANYBUS | SYSTEM
Peripherials | HMS | Anybus | Blackfin | ABCC_DriverHandler | 1 | 0x07 | 0 | 0 | 0x070011 | ERROR_CODES::ANY_EXCPT | ABCC_EXCPT_INV_DEV_ADDR | Invalid device address | Blackfin | Extern | [6 empty] | CFG_ANYBUS | SYSTEM
Peripherials | HMS | Anybus | Blackfin | ABCC_DriverHandler | 2 | 0x07 | 0 | 0 | 0x070012 | ERROR_CODES::ANY_EXCPT | ABCC_EXCPT_INV_COM_SETTINGS | Invalid communication settings | Blackfin | Extern | [6 empty] | CFG_ANYBUS | SYSTEM
Peripherials | HMS | Anybus | Blackfin | ABCC_DriverHandler | 3 | 0x07 | 0 | 0 | 0x070013 | ERROR_CODES::ANY_EXCPT | ABCC_EXCPT_MAJ_UNREC_APP_EVNT | Major unrecoverable application event | Blackfin | Extern | [6 empty] | CFG_ANYBUS | SYSTEM
Peripherials | HMS | Anybus | Blackfin | ABCC_DriverHandler | 4 | 0x07 | 0 | 0 | 0x070014 | ERROR_CODES::ANY_EXCPT | ABCC_EXCPT_WAIT_APP_RESET | Waiting for application reset | Blackfin | Extern | [6 empty] | CFG_ANYBUS | SYSTEM
Peripherials | HMS | Anybus | Blackfin | ABCC_DriverHandler | 5 | 0x07 | 0 | 0 | 0x070015 | ERROR_CODES::ANY_EXCPT | ABCC_EXCPT_INV_PRD_CFG | Invalid process data configuration | Blackfin | Extern | [6 empty] | CFG_ANYBUS | SYSTEM
Peripherials | HMS | Anybus | Blackfin | ABCC_DriverHandler | 6 | 0x07 | 0 | 0 | 0x070016 | ERROR_CODES::ANY_EXCPT | ABCC_EXCPT_INV_APP_RESPONSE | Invalid application response | Blackfin | Extern | [6 empty] | CFG_ANYBUS | SYSTEM
Peripherials | HMS | Anybus | Blackfin | ABCC_DriverHandler | 7 | 0x07 | 0 | 0 | 0x070017 | ERROR_CODES::ANY_EXCPT | ABCC_EXCPT_NVS_CHECKSUM_ERROR | Non-volatile memory checksum error | Blackfin | Extern | [6 empty] | CFG_ANYBUS | SYSTEM
Peripherials | HMS | Anybus | Blackfin | ABCC_DriverHandler | 8 | 0x07 | 0 | 0 | 0x070018 | ERROR_CODES::ANY_EXCPT | ABCC_EXCPT_NETWORK_SPECIFIC_1 | Network specific exception code: 0x01 | Blackfin | Extern | [6 empty] | CFG_ANYBUS | SYSTEM
Peripherials | HMS | Anybus | Blackfin | ABCC_DriverHandler | 9 | 0x07 | 0 | 0 | 0x070019 | ERROR_CODES::ANY_EXCPT | ABCC_EXCPT_NETWORK_SPECIFIC_2 | Network specific exception code: 0x02 | Blackfin | Extern | [6 empty] | CFG_ANYBUS | SYSTEM
Peripherials | HMS | Anybus | Blackfin | ABCC_DriverHandler | 10 | 0x07 | 0 | 0 | 0x07001A | ERROR_CODES::ANY_EXCPT | ABCC_EXCPT_NETWORK_SPECIFIC_3 | Network specific exception code: 0x03 | Blackfin | Extern | [6 empty] | CFG_ANYBUS | SYSTEM
Peripherials | HMS | Anybus | Blackfin | ABCC_DriverHandler | 11 | 0x07 | 0 | 0 | 0x07001B | ERROR_CODES::ANY_EXCPT | ABCC_EXCPT_NETWORK_SPECIFIC_4 | Network specific exception code: 0x04 | Blackfin | Extern | [6 empty] | CFG_ANYBUS | SYSTEM
Peripherials | HMS | Anybus | Blackfin | ABCC_DriverHandler | 12 | 0x07 | 0 | 0 | 0x07001C | ERROR_CODES::ANY_EXCPT | ABCC_EXCPT_NETWORK_SPECIFIC_5 | Network specific exception code: 0x05 | Blackfin | Extern | [6 empty] | CFG_ANYBUS | SYSTEM
Peripherials | HMS | Anybus | Blackfin | ABCC_DriverHandler | 13 | 0x07 | 0 | 0 | 0x07001D | ERROR_CODES::ANY_EXCPT | ABCC_EXCPT_NETWORK_SPECIFIC_6 | Network specific exception code: 0x06 | Blackfin | Extern | [6 empty] | CFG_ANYBUS | SYSTEM
Peripherials | HMS | Anybus | Blackfin | ABCC_DriverHandler | 14 | 0x07 | 0 | 0 | 0x07001E | ERROR_CODES::ANY_EXCPT | ABCC_EXCPT_NETWORK_SPECIFIC_7 | Network specific exception code: 0x07 | Blackfin | Extern | [6 empty] | CFG_ANYBUS | SYSTEM
ESS | Samsung Mega 3.3 | Rack Group | Modbus | 30012 | 0 | 0x05 | 0 | 3 | 0x050300 | ERROR_CODES::ESS::SAMSUNG::MEGA_33::SYSTEM | COMMUNICATION_FAULT | Communication Fault | Blackfin | BOOL |  | 10 |  |  |  |  | SHUTDOWN | SINGLE
ESS | Samsung Mega 3.3 | Rack Group | Modbus | 30012 | 10 | 0x05 | 0 | 3 | 0x05030A | ERROR_CODES::ESS::SAMSUNG::MEGA_33::SYSTEM | IMBALANCE_ALARM | Imbalance alarm | Blackfin | Extern | [6 empty] | WARNING | SINGLE
ESS | Samsung Mega 3.3 | Rack Group | Modbus | 30012 | 11 | 0x05 | 0 | 3 | 0x05030B | ERROR_CODES::ESS::SAMSUNG::MEGA_33::SYSTEM | IMBALANCE_STOP | Imbalance error | Blackfin | Extern | [6 empty] | WARNING | SINGLE
ESS | Samsung Mega 3.3 | Rack Group | Modbus | 30012 | 12 | 0x05 | 0 | 3 | 0x05030C | ERROR_CODES::ESS::SAMSUNG::MEGA_33::SYSTEM | VOLTAGE_DIFF | DC voltage not synchronized | Blackfin | Extern | [6 empty] | WARNING | SINGLE | ¦Target Voltage - System Voltage¦<= Setting Voltage-> Valid (DC contactor ON) ¦Target Voltage - System Voltage¦> Setting Voltage -> Invalid (DC contactor OFF)
ESS | Samsung Mega 3.3 | Rack Group | Modbus | 30012 | 13 | 0x05 | 0 | 3 | 0x05030D | ERROR_CODES::ESS::SAMSUNG::MEGA_33::SYSTEM | NO_CONTACTOR_ON_COMMAND | Close contactor command timeout | Blackfin | Extern | [6 empty] | WARNING | SINGLE | ¦Target Voltage - System Voltage¦<= Setting Voltage -> Valid (DC contactor ON) Not receive "Command On" within a Setting Time -> Invalid (DC contactor OFF)
ESS | Samsung Mega 3.3 | Rack | Blackfin | CSamsungMega33Rack | 0 | 0x04 | 0 | 2 | 0x040200 | ERROR_CODES::ESS::GROUP::RACK | CLOSE_BLOCKED | Contactor closing blocked | Blackfin | HIGH | 3 | 0 |  |  |  |  | WARNING | SINGLE | Max Cell T >= 65*C, 5sec
ESS | Samsung Mega 3.3 | Rack | Blackfin | CSamsungMega33Rack | 1 | 0x04 | 0 | 2 | 0x040201 | ERROR_CODES::ESS::GROUP::RACK | OPEN_BLOCKED | Contactor opening blocked | Blackfin | HIGH | 0.1 | 0 |  |  |  |  | WARNING | SINGLE | Max Cell T >= 65*C, 5sec
ESS | Samsung Mega 3.3 | Rack | Modbus | 30061+(#r-1)*26 | 1 | 0x04 | 0 | 3 | 0x040301 | ERROR_CODES::ESS::SAMSUNG::MEGA_33::RACK::TRIP | CELL_OVERTEMPERATURE | Cell Overtemperature Trip | Blackfin | Extern | [6 empty] | SHUTDOWN | SINGLE | Max Cell T >= 65*C, 5sec
ESS | Samsung Mega 3.3 | Rack | Modbus | 30061+(#r-1)*26 | 2 | 0x04 | 0 | 3 | 0x040302 | ERROR_CODES::ESS::SAMSUNG::MEGA_33::RACK::TRIP | CELL_UNDERVOLTAGE | Cell Undervoltage Trip | Blackfin | Extern | [6 empty] | SHUTDOWN | SINGLE | Min Cell V <= 2.50V, 3sec
ESS | Samsung Mega 3.3 | Rack | Modbus | 30061+(#r-1)*26 | 3 | 0x04 | 0 | 3 | 0x040303 | ERROR_CODES::ESS::SAMSUNG::MEGA_33::RACK::TRIP | CELL_OVERVOLTAGE | Cell Overvoltage Trip | Blackfin | Extern | [6 empty] | SHUTDOWN | SINGLE | Max Cell V >= 4.20V, 5sec
ESS | Samsung Mega 3.3 | Rack | Modbus | 30061+(#r-1)*26 | 7 | 0x04 | 0 | 3 | 0x040307 | ERROR_CODES::ESS::SAMSUNG::MEGA_33::RACK::TRIP | RACK_UNDERVOLTAGE | Rack Undervoltage Trip | Blackfin | Extern | [6 empty] | SHUTDOWN | SINGLE | Rack V <= *Reference level, 3sec
ESS | Samsung Mega 3.3 | Rack | Modbus | 30061+(#r-1)*26 | 8 | 0x04 | 0 | 3 | 0x040308 | ERROR_CODES::ESS::SAMSUNG::MEGA_33::RACK::TRIP | RACK_OVERVOLTAGE | Rack Overvoltage Trip | Blackfin | Extern | [6 empty] | SHUTDOWN | SINGLE | Rack V >= *Reference level, 5sec
ESS | Samsung Mega 3.3 | Rack | Modbus | 30061+(#r-1)*26 | 9 | 0x04 | 0 | 3 | 0x040309 | ERROR_CODES::ESS::SAMSUNG::MEGA_33::RACK::TRIP | RACK_COMM_FAULT | Rack Communication Fault | Blackfin | Extern | [6 empty] | SHUTDOWN | SINGLE | No response from Rack, 30sec
ESS | Samsung Mega 3.3 | Rack | Modbus | 30061+(#r-1)*26 | 10 | 0x04 | 0 | 3 | 0x04030A | ERROR_CODES::ESS::SAMSUNG::MEGA_33::RACK::TRIP | TRAY_COMM_FAULT | Tray Communication Fault | Blackfin | Extern | [6 empty] | SHUTDOWN | SINGLE | No response from Tray, 30sec
ESS | Samsung Mega 3.3 | Rack | Modbus | 30061+(#r-1)*26 | 11 | 0x04 | 0 | 3 | 0x04030B | ERROR_CODES::ESS::SAMSUNG::MEGA_33::RACK::TRIP | OVERCURRENT | Overcurrent Trip | Blackfin | Extern | [6 empty] | SHUTDOWN | SINGLE | Charge : Current >= 205A, 1sec // Discharge : Current >= 335A, 1sec
ESS | Samsung Mega 3.3 | Rack | Modbus | 30061+(#r-1)*26 | 13 | 0x04 | 0 | 3 | 0x04030D | ERROR_CODES::ESS::SAMSUNG::MEGA_33::RACK::TRIP | ADDITIONAL_PROTECTION | Additional Protection Tray | Blackfin | Extern | [6 empty] | SHUTDOWN | SINGLE | Rack OVP or OCP fault by 2nd MCU
ESS | Samsung Mega 3.3 | Rack | Modbus | 30061+(#r-1)*26 | 14 | 0x04 | 0 | 3 | 0x04030E | ERROR_CODES::ESS::SAMSUNG::MEGA_33::RACK::TRIP | DC_CONTACTOR_FAULT | DC Contactor Fault | Blackfin | Extern | [6 empty] | SHUTDOWN | SINGLE | Current >= 300mA even if the contactor is opened, 3sec
ESS | Samsung Mega 3.3 | Rack | Modbus | 30061+(#r-1)*26 | 15 | 0x04 | 0 | 3 | 0x04030F | ERROR_CODES::ESS::SAMSUNG::MEGA_33::RACK::TRIP | DC_CONTACTOR_SENSOR_FAULT | DC Contactor Sensor Fault | Blackfin | Extern | [6 empty] | SHUTDOWN | SINGLE | Feedback Status of contactor ≠ Contactor command, 3sec
ESS | Samsung Mega 3.3 | Rack | Modbus | 30062+(#r-1)*26 | 0 | 0x04 | 0 | 3 | 0x040310 | ERROR_CODES::ESS::SAMSUNG::MEGA_33::RACK::WARNING | CELL_UNDERTEMPERATURE | Warning: Cell Undertemperature | Blackfin | Extern |  |  |  |  | x |  | WARNING | SINGLE | Min Cell T <= -21*C, 3sec
ESS | Samsung Mega 3.3 | Rack | Modbus | 30062+(#r-1)*26 | 1 | 0x04 | 0 | 3 | 0x040311 | ERROR_CODES::ESS::SAMSUNG::MEGA_33::RACK::WARNING | CELL_OVERTEMPERATURE | Warning: Cell Overtemperature | Blackfin | Extern | [6 empty] | WARNING | SINGLE | Max Cell T >= 60*C, 3sec
ESS | Samsung Mega 3.3 | Rack | Modbus | 30062+(#r-1)*26 | 2 | 0x04 | 0 | 3 | 0x040312 | ERROR_CODES::ESS::SAMSUNG::MEGA_33::RACK::WARNING | CELL_UNDERVOLTAGE | Warning: Cell Undervoltage | Blackfin | Extern | [6 empty] | WARNING | SINGLE | Min Cell V <= 2.70V, 1sec
ESS | Samsung Mega 3.3 | Rack | Modbus | 30062+(#r-1)*26 | 3 | 0x04 | 0 | 3 | 0x040313 | ERROR_CODES::ESS::SAMSUNG::MEGA_33::RACK::WARNING | CELL_OVERVOLTAGE | Warning: Cell Overvoltage | Blackfin | Extern | [6 empty] | WARNING | SINGLE | Max Cell V >= 4.18V, 3sec
ESS | Samsung Mega 3.3 | Rack | Modbus | 30062+(#r-1)*26 | 4 | 0x04 | 0 | 3 | 0x040314 | ERROR_CODES::ESS::SAMSUNG::MEGA_33::RACK::WARNING | RACK_VOLTAGE_ERROR | Warning: Rack voltage deviates from sum | Blackfin | Extern | [6 empty] | WARNING | SINGLE | (Rack Voltage - Sum of cell voltage) >= 77V, 3 sec
ESS | Samsung Mega 3.3 | Rack | Modbus | 30062+(#r-1)*26 | 5 | 0x04 | 0 | 3 | 0x040315 | ERROR_CODES::ESS::SAMSUNG::MEGA_33::RACK::WARNING | CELL_VOLTAGE_IMBALANCE | Warning: Cell Voltage Imbalance | Blackfin | Extern |  |  |  |  | x |  | WARNING | SINGLE | Max Cell >= 3.5V & d cell V >= 300mV, 5sec
ESS | Samsung Mega 3.3 | Rack | Modbus | 30062+(#r-1)*26 | 6 | 0x04 | 0 | 3 | 0x040316 | ERROR_CODES::ESS::SAMSUNG::MEGA_33::RACK::WARNING | CELL_TEMPERATURE_IMBALANCE | Warning: Cell Temperature Imbalance | Blackfin | Extern | [6 empty] | WARNING | SINGLE | dCell T >= 20*C, 30sec
ESS | Samsung Mega 3.3 | Rack | Modbus | 30062+(#r-1)*26 | 7 | 0x04 | 0 | 3 | 0x040317 | ERROR_CODES::ESS::SAMSUNG::MEGA_33::RACK::WARNING | RACK_UNDERVOLTAGE | Warning: Rack Undervoltage | Blackfin | Extern | [6 empty] | WARNING | SINGLE | Rack V <= *Reference level, 1sec
ESS | Samsung Mega 3.3 | Rack | Modbus | 30062+(#r-1)*26 | 8 | 0x04 | 0 | 3 | 0x040318 | ERROR_CODES::ESS::SAMSUNG::MEGA_33::RACK::WARNING | RACK_OVERVOLTAGE | Warning: Rack Overvoltage | Blackfin | Extern | [6 empty] | WARNING | SINGLE | Rack V >= *Reference level, 3sec
ESS | Samsung Mega 3.3 | Rack | Modbus | 30062+(#r-1)*26 | 9 | 0x04 | 0 | 3 | 0x040319 | ERROR_CODES::ESS::SAMSUNG::MEGA_33::RACK::WARNING | RACK_COMM_FAULT | Warning: Rack Communication Fault | Blackfin | Extern | [6 empty] | WARNING | SINGLE | No response from Rack, 10sec
ESS | Samsung Mega 3.3 | Rack | Modbus | 30062+(#r-1)*26 | 10 | 0x04 | 0 | 3 | 0x04031A | ERROR_CODES::ESS::SAMSUNG::MEGA_33::RACK::WARNING | TRAY_COMM_FAULT | Warning: Tray Communication Fault | Blackfin | Extern | [6 empty] | WARNING | SINGLE | No response from Tray, 10sec
ESS | Samsung Mega 3.3 | Rack | Modbus | 30062+(#r-1)*26 | 11 | 0x04 | 0 | 3 | 0x04031B | ERROR_CODES::ESS::SAMSUNG::MEGA_33::RACK::WARNING | OVERCURRENT | Warning: Rack Overcurrent | Blackfin | Extern | [6 empty] | WARNING | SINGLE | Charge : Current >= 200A, 3sec // Discharge : Current >= 315A, 3sec
ESS | Samsung Mega 3.3 | Rack | Modbus | 30062+(#r-1)*26 | 12 | 0x04 | 0 | 3 | 0x04031C | ERROR_CODES::ESS::SAMSUNG::MEGA_33::RACK::WARNING | SOC_FULL | Rack Charge Completed | Blackfin | Extern | [6 empty] | INFO | SINGLE | Just before SOC 100%
ESS | Samsung Mega 3.3 | Rack | Modbus | 30062+(#r-1)*26 | 13 | 0x04 | 0 | 3 | 0x04031D | ERROR_CODES::ESS::SAMSUNG::MEGA_33::RACK::WARNING | SENSOR_COMMUNICATION_FAULT | Warning: Current Sensor Communication Fault | Blackfin | Extern | [6 empty] | WARNING | SINGLE | Sensor Communication Pending, 3sec
ESS | Samsung Mega 3.3 | Rack | Modbus | 30062+(#r-1)*26 | 14 | 0x04 | 0 | 3 | 0x04031E | ERROR_CODES::ESS::SAMSUNG::MEGA_33::RACK::WARNING | CHARGE_OVERCURRENT | Warning: Charge Current Limit Exceeded | Blackfin | Extern | [6 empty] | WARNING | SINGLE | Exceed Permissive Current Value, 5sec
ESS | Samsung Mega 3.3 | Rack | Modbus | 30062+(#r-1)*26 | 15 | 0x04 | 0 | 3 | 0x04031F | ERROR_CODES::ESS::SAMSUNG::MEGA_33::RACK::WARNING | FAN_FAULT | Warning: Fan Fault | Blackfin | Extern | [6 empty] | WARNING | SINGLE | One more fan not operated under active circumstance, 5sec